ENCLOSURE 2

Guaranteed parameters

The below stated Enclosure 2 – Guaranteed Parameters shall be prepared and submitted by the economic operator / participant in Volume C2 of the tender (as an enclosure of the draft contract for work) in accordance with the contracting authority’s instructions for preparing Volume C2 contained in Part 4 of the Procurement Documents.

Legend:

Failure to achieve these highlighted guaranteed values will be grounds for seeking the contractual fine – see Article 44.2 of the contract.

Failure to achieve these highlighted limit values may be grounds for not accepting the work and / or withdrawal from the contract - see Article 44.2.73 of the contract.

Contents

1	Input Conditions	4

2	Guaranteed parameters	4

2.1	Waste incineration	5

2.2	Flue gas treatment	7

2.3	Specific consumption of reagents	8

2.4	Flue gas treatment wastewater quality	12

2.5	Waste produced by the technological process	13

2.6	Steam production and water consumption	14

2.7	Boiler thermal efficiency at design point “D”	14

2.8	Use of energy contained in waste for to generate electricity and heat for external consumers	15

2.9	Vacuum drop	16

2.10	Service life of boiler components	17

2.11	Availability of the work	18

2.11.1	Annual capacity availability of steam production [VDP ]	19

2.11.2	Availability of operation (steam production)	20

2.11.3	Availability of steam-water cycle (VWSC)	20

2.12	Uninterrupted boiler operation time	21

2.13	Noisiness	22

3	Guarantee measurement conditions	23

# Input Conditions

The guaranteed values shall be proven at the guarantee tests at:

incineration of waste according to Chapter 1.7.1 of Enclosure 1 of the contract,

stable operation without the use of additional fuel (natural gas)

during verifications of the guaranteed parameters, it shall not be possible to modify the machinery setup; the systems shall be operated in automatic mode without manual interventions.

reference temperature of the primary air intake: +10°C,

reference temperature of the secondary air intake: +30°C,

outer cooling circuit cooling water temperature at the entry into the TG condenser shall be +20°C,

temperature of the return circulating water of the hot water pipe at the entrance to the facility: +60°C.

guarantee test "A" will be performed on a clean boiler.

guarantee test "B" will be performed on the boiler after 7,500 hours of operation since boiler cleaning, the purchaser reserves the right to reduce the number of operating hours since boiler cleaning for test "B".

# Guaranteed parameters

The Contractor shall be liable to the Purchaser for the fact that the work delivered will meet the below stated parameters and functions:

## Waste incineration

The operating range of the equipment delivered by the Contractor must cover all the operation points of the below stated firing capacity diagram or must be wider.

Legend:

Basic design point:		point D

Minimum furnace heat capacity:	30.00 MW

Permanent furnace heat capacity:	52.10 MW

Top (Peak) furnace heat capacity:	57.31 MW

Minimum amount of waste combusted (weight flow):		11.00 t/h

Permanent amount of waste combusted (weight flow):		18.75 t/h

Top (Peak) amount of waste combusted (weight flow):		21.56 t/h

The operating range of the facility shall be proved by means of the following guaranteed values:

(Test) proving conditions:

The input conditions according to Chapter  1 shall apply,

It is necessary to comply with nominal parameters of steam (pressure, temperature),

The emission values must meet the requirements provided for in Chapter 2.3 in the entire range of the firing capacity diagram and for all the time of the test,

The fuel heat capacity will be detected indirectly from the heat (thermal) output measured on the outlet from the boiler and from the boiler efficiency measured.

Guaranteed values:

| Parameter |  | Unit | Limit value |
| --- | --- | --- | --- |
| 2.1.1 | Continuous heat output of the combustion section | MWt | 52.10 |
| 2.1.2 | Minimum heat output of the combustion section | MWt | 30.00 |
| 2.1.3 | Minimum amount of waste combusted (mass flow) | t/h | 11.00 |
| 2.1.4 | Permanent amount of waste combusted (mass flow) | t/h | 18.75 |
| 2.1.5 | Peak amount of waste combusted (mass flow): | t/h | 21.56 |
| 2.1.6 | Flue gas holding time at a temperature of at least 850°C in the entire range of the firing capacity diagram (downstream of the last air inlet) | sec | ≥ 2 |
| 2.1.7 | Under-burning in cinder (slag) and grate through fraction in the entire range of the firing capacity diagram; related to the dry matter as annealing loss | % | ≤ 3 |
| 2.1.8 | Peak thermal output of the combustion section | MWt | 57.31 |

## Flue gas treatment

The limit values are set by COMMISSION IMPLEMENTING DECISION (EU) 2019/2010 of 12 November 2019 laying down conclusions on best available techniques (BAT) for waste incineration pursuant to Directive 2010/75/EU of the European Parliament and of the Council.

For the purposes of improving the quality of the work, the client decided to tighten the limit values of averages 2.2.1 to 2.2.13 according to the table below. At the same time, the limit values of pollutant concentrations in released flue gases as contained in Decree 415/2012 Coll. will be met.

(Test) proving conditions:

The input conditions according to Chapter 1,

Measurement will be performed in accordance with Act No. 201/2012 Coll. as amended, Decree 415/2012 Coll. as amended and Directive 2010/75/EU of the European Parliament and of the Council on industrial emissions,

The below specified guaranteed values shall apply to all operating states of the work in the entire range of the firing capacity diagram, including dynamical changes in the output capacity

The values shall apply to dry gas (273.15 K, 101.32 kPa); the conversion shall be carried out to 11% of voluminous O2 in the case that the actual content of O2 in flue gas is higher

In the case of emission limits the measuring tolerance shall not apply.

Guaranteed values of released flue gases

| Type of emission |  | Unit | Period for determining averages | Limit values of averages |
| --- | --- | --- | --- | --- |
| 2.2.1 | Dust | mg/Nm3 | Daily average | < 4 |
| 2.2.2 | Cadmium, thallium (Cd+Tl) | mg/Nm3 | Average for the sampling interval | ≤ 0.016 |
| 2.2.3 | Other heavy metals, total (Sb, As, Pb, Cr, Co, Cu, Mn, Ni, V) | mg/Nm3 | Average for the sampling interval | ≤ 0.24 |
| 2.2.4 | Hydrogen chloride (HCl) | mg/Nm3 | Daily average | < 5 |
| 2.2.5 | Hydrogen fluoride (HF) | mg/Nm3 | Daily average or average for the sampling interval | < 0.8 |
| 2.2.6 | Sulphur dioxide (SO2) | mg/Nm3 | Daily average | ≤ 24 |
| 2.2.7 | Oxides of nitrogen (NOx as NO2) | mg/Nm3 | Daily average | ≤ 70 |
| 2.2.8 | Carbon monoxide (CO) | mg/Nm3 | Daily average | ≤ 30 |
| 2.2.9 | Ammonia (NH3) | mg/Nm3 | Daily average | ≤ 8 |
| 2.2.10 | TVOC | mg/Nm3 | Daily average | ≤ 8 |
| 2.2.11 | PCDD/F | ng I-TEQ/Nm3 | Average for the sampling interval | ≤ 0.04 |
|  |  | ng I-TEQ/Nm3 | Long-term sampling interval | ≤ 0.048 |
| 2.2.12 | PCDD/F + PCB with dioxin effect | ng WHQ-TEQ/Nm3 | Average for the sampling interval | ≤ 0.06 |
|  |  | ng WHQ-TEQ/Nm3 | Long-term sampling interval | ≤ 0.064 |
| 2.2.13 | Mercury and its compounds (Hg) | mg/Nm3 | Daily average for the sampling interval | ≤ 0.016 |
|  |  | mg/Nm3 | Long-term sampling interval | ≤ 0.010 |

## Specific consumption of reagents

Type and concentration of the reducing agent to reduce oxides of nitrogen

| Reducing agent – chemical formula of the active substance | … (to be completed by the Participant) |
| --- | --- |
| Concentration of the active substance [%] | … (to be completed by the Participant) |
| Note *) | … (to be completed by the Participant) |

*)	In the note the Participant shall specify the manner in which the concentration of the active substance is given (mass or volume concentration %, whether it’s a solution, reference to an appendix – product safety data sheet etc.)

Guaranteed values:

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.3.1 | Specific consumption of the reducing agent in a 100% concentration [kg/t of waste] | kg/t of waste | ≤ … to be completed by the Participant |

Consumption of the reducing agent will be specified for continuous thermal output of the combustion section and assessed over a 5-day period of operation of the work (to be specified in the Guarantee Measurement project), whereby concurrent delivery of the guaranteed values per 2.2.7 is a condition for the fulfilment of the guaranteed parameter.

Specific consumption of reagents for capturing acid components of flue gases and heavy metals

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.3.2 | Specific consumption of NaOH | kg/h | ≤ … to be completed by the Participant |
| 2.3.3 | Specific consumption of Ca(OH)2 | kg/h | ≤ … to be completed by the Participant |
| 2.3.4 | Specific consumption of activated carbon | kg/h | ≤ … to be completed by the Participant |
| 2.3.5 | Specific consumption of NaHCO3 | kg/h | ≤ … to be completed by the Participant |
| 2.3.6 | Specific consumption of CaO | kg/h | ≤ … to be completed by the Participant |
| 2.3.7 | Specific consumption of NaCl (100 %) | kg/h | ≤ … to be completed by the Participant |
| 2.3.8 | Specific consumption of CaCO3 | kg/h | ≤ … to be completed by the Participant |

Note: if the Participant does not use any of the specified reagents in the proposed flue gas treatment design, it shall specify a consumption value of 0 for each such guaranteed parameter.

If the Participant uses other reagents in the proposed flue gas treatment design that are not specified above, they shall add such reagents along with a guaranteed consumption value in the following table Other Reagents for Capturing Acid Components of Flue Gases and Heavy Metals:

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.3.9.1 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.9.2 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.9.3 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.9.n | Specific consumption … | kg/h | ≤ … to be completed by the Participant |

Specific consumption of reagents for wastewater treatment and feed water chemical treatment

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.3.10 | Specific consumption of HCl (30%) | kg/h | ≤ … to be completed by the Participant |
| 2.3.11 | Specific consumption of Na2S (13%) | kg/h | ≤ … to be completed by the Participant |
| 2.3.12 | Specific consumption of FeCl3 (40%) | kg/h | ≤ … to be completed by the Participant |
| 2.3.13 | Specific consumption of Cyklohexylamine (99 %) | kg/h | ≤ … to be completed by the Participant |
| 2.3.14 | Specific consumption of Ca(OH)2 | kg/h | ≤ … to be completed by the Participant |

If the Participant uses other reagents in the proposed water treatment design that are not specified above, they shall add such reagents along with a guaranteed consumption value in the following table Other Reagents for Wastewater Treatment and Feed Water Chemical Treatment:

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.3.15.1 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.15.2 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.15.3 | Specific consumption … | kg/h | ≤ … to be completed by the Participant |
| 2.3.15.n | Specific consumption … | kg/h | ≤ … to be completed by the Participant |

(Test) proving conditions:

Consumption of substances will be assessed over a 5-day period of operation of the work (to be specified in the Guarantee Measurement project), whereby concurrent delivery of the guaranteed values per 2.2. and 2.4 is a condition for the fulfilment of the guaranteed parameter.

The participant shall specify the guaranteed values for continuous heat output of the combustion section (basic design point D of firing capacity diagram) and fuel parameters defined in part no. 4 - Forms and detailed instructions, VOLUME C13 - TECHNICAL SPECIFICATION OF THE contractor - paragraph no. 9 in the “Average value” column and on that basis established reference parameters of the flue gas** at the boiler outlet (before entering the flue gas cleaning system) listed below:

| Quantities | Unit | Data |
| --- | --- | --- |
| Flue gas temperature | °C | … to be completed by the Participant |
| H2O content | % vol. | … to be completed by the Participant |
| O2 content | % vol. | … to be completed by the Participant |
| Amount of flue gas at the boiler outlet | Nm3/h | … to be completed by the Participant |
| Particulate at the boiler outlet | mg/Nm3 | … to be completed by the Participant |
| HCl | mg/Nm3 | … to be completed by the Participant |
| HF | mg/Nm3 | … to be completed by the Participant |
| SOx corresponding to SO2 | mg/Nm3 | … to be completed by the Participant |
| Sb+As+Pb+Cr+Co+Cu+Mn+Ni+V | mg/Nm3 | 20 |
| NOx as NO2*** | mg/Nm3 | … to be completed by the Participant |
| Zn | mg/Nm3 | 1.50 |
| Cd+Tl | mg/Nm3 | 1.00 |
| Hg | mg/Nm3 | 0.40 |
| PCDD/PCDF | ng/Nm3 | 3.00 |

To evaluate the specific consumptions according to Chapter 2.3, correction curves will be used in case of deviation of the values of emissions in the flue gases at the boiler outlet from the above-mentioned reference values. The contractor shall prepare these correction curves in the Guarantee Measurement Project.

Notes:

**) The values apply to dry gas, normal conditions (273.15 K, 101.3 kPa), converted to 11% by volume O2.

***) NOx as NO2 does not represent the reference value at the boiler outlet but serves as a guide value for calculating the amount of reagent for DENOx.

## Flue gas treatment wastewater quality

The technological chain of the waste-to energy process shall be equipped with a flue gas treatment with a subsequent treatment of the process waters.

(Test) proving conditions:

The input conditions according to Chapter 1,

The below specified guaranteed values shall apply to all operating states of the work in the entire range of the firing capacity diagram, including dynamical changes in the output capacity,

In the case of emission limits the measuring tolerance shall not apply.

Limit values of pollutant content in discharged waters are set by COMMISSION IMPLEMENTING DECISION (EU) 2019/2010 of 12 November 2019 laying down conclusions on best available techniques (BAT) for waste incineration pursuant to Directive 2010/75/EU of the European Parliament and of the Council.

Guaranteed values:

| Industrial sector: waste incineration Indicator |  | Unit | Limit values |
| --- | --- | --- | --- |
| 2.4.1 | Total insoluble solids (TSS) | mg/l | 30 |
| 2.4.2 | Total organic carbon (TOC) | mg/l | 40 |
| 2.4.3 | pH | - | 6.5 - 8.5 |
| 2.4.4 | Mercury and its compounds expressed as Hg | mg/l | 0.01 |
| 2.4.5 | Cadmium and its compounds expressed as Cd | mg/l | 0.02 |
| 2.4.6 | Thallium and its compounds expressed as Tl | mg/l | 0.02 |
| 2.4.7 | Arsenic and its compounds expressed as As | mg/l | 0.05 |
| 2.4.8 | Lead and its compounds expressed as Pb | mg/l | 0.05 |
| 2.4.9 | Chromium and its compounds expressed as Cr | mg/l | 0.1 |
| 2.4.10 | Copper and its compounds expressed as Cu | mg/l | 0.15 |
| 2.4.11 | Nickel and its compounds expressed as Ni | mg/l | 0.15 |
| 2.4.12 | Zinc and its compounds expressed as Zn | mg/l | 0.5 |
| 2.4.13 | Antimony and its compounds expressed as Sb | mg/l | 0.9 |
| 2.4.14 | Ammonium nitrogen (N-NH4+) | mg/l | 5.5 |
| 2.4.15 | Sulphates (SO42-) | mg/l | 1000 |
| 2.4.16 | Total of PCDD/F | ng/l | 0.05 |
| 2.4.17 | RAS – Soluble inorganic salts | g/l | 15 *) |

*) 	The contractor shall adjust the amount of the cleaned process waters from flue gas treatment in such a way the RAS (dissolved inorganic salts) concentration does not exceed 15 g/l.

## Waste produced by the technological process

(Test) proving conditions:

The input conditions according to Chapter 1. and 2.3 shall apply.

The values shall be taken from design point D according to chapter 2.1

| Parameter |  | Unit | Guaranteed value |
| --- | --- | --- | --- |
| 2.5.1 | Slag production | kg/h | ≤ … to be completed by the Participant |
| 2.5.2 | Production of washed fly ash – classified as other waste | kg/h | ≤ … to be completed by the Participant |
| 2.5.3 | Production of filter cake – classified as other waste | kg/h | ≤ … to be completed by the Participant |
| 2.5.4 | Production of other waste (not specified above) and classified as other waste | kg/h | ≤ … to be completed by the Participant |
| 2.5.5 | Production of filter cake – classified as hazardous waste (per Decree 8/2021 Coll.) | kg/h | ≤ … to be completed by the Participant |
| 2.5.6 | Production of bag filter dust – classified as hazardous waste (per Decree 8/2021 Coll.) | kg/h | ≤ … to be completed by the Participant |
| 2.5.7 | Production of other (not specified above) hazardous waste (per Decree 8/2021 Coll.) | kg/h | ≤ … to be completed by the Participant |

## Steam production and water consumption

(Test) proving conditions:

The input conditions according to Chapter 1,

the values achieved shall not be worse than limit values,

superheated steam pressure at the boiler outlet … (to be completed by the Participant in a range of 4.2-6.0) MPa abs.,

The below specified guaranteed values stand for operational states of the work in the range of 80% - 100% of fuel heat capacity of the firing capacity diagram, including dynamical changes in the output capacity and required overload capacity (design points C‘, D‘, E‘) according to chapter 2.1,

The flue gas temperature on first superheater (downstream of the flue gases) may not exceed 620°C.

Guaranteed values:

| Parameter |  | Unit | Limit value | Note |
| --- | --- | --- | --- | --- |
| 2.6.1 | Rated temperature of overheated steam on the boiler outlet | °C | 408 | permitted oscillation ± 5°C |
| 2.6.2 | Oscillation of the thermal power output of the boiler | % | max. ± 5 % | from the mean value of the steam power in the last hour |

| Parameter |  | Unit | Limit value | Guaranteed value |
| --- | --- | --- | --- | --- |
| 2.6.3 | Clarified water consumption | m3/h | - | ≥ … (to be completed by the Participant) |
| 2.6.4 | Demineralised water consumption | m3/h | - | ≥ … (to be completed by the Participant) |
| 2.6.5 | Raw water consumption | m3/h | - | ≥ … (to be completed by the Participant) |

## Boiler thermal efficiency at design point “D”

(Test) proving conditions:

The input conditions according to Chapter 1,

Boiler thermal efficiency shall be determined in accordance with the European standard created for the specific case of facilities for energy use of waste “Acceptance Testing of Waste Incineration Plants with Grate Firing System, Guideline edition 04/2000 by FBDR” with the use of the methodology and principles of ČSN EN 12952-15 – Water-tube boilers and auxiliary installations – Part 15: Acceptance tests.

With regard to the highly variable composition of the fuel (waste) composition, the indirect method based on ascertainment of thermal losses shall be used.

The boiler thermal efficiency shall be established at the operation state 52.1 MWt – permanent thermal power of the furnace

Guaranteed value:

| Parameter |  | Unit | Limit value | Guaranteed value |
| --- | --- | --- | --- | --- |
| 2.7.1 | Thermal efficiency of the boiler (η boiler) | % | ≥ 80 | ≥ … To be completed by the Participant |

## Use of energy contained in waste for to generate electricity and heat for external consumers

(Test) proving conditions:

The input conditions according to Chapter 1,

The test shall last for 24 hours.

Boiler thermal output shall be regulated during the test to the value corresponding to the nominal (rated) fuel heat capacity (52.1 MWt) by conversion using the efficiency measured according to Chapter  2.7.,

The value of electricity supply will be verified using the invoicing meter at the transfer point to the 35 kV distribution network and taking a reading of the output power at the generator terminals,

During tests all the installed equipment shall be in normal operation; it is not allowed to artificially reduce own power consumption during the test by specific measures,  e.g. altering the waste processing organization (restricted shredder operation and waste homogenization),

The parameter value will be verified for the following two operation states of the EVO:

- State 1:

TG in a fully condensation operation mode (steam production covering own consumption only)

no heat is supplied to the hot-water piping system

- State 2:

TG in the off-take operation mode, heat supply to the hot-water piping system: 32.0 MWt

Guaranteed values:

| Parameter |  | Unit | Limit value | Guaranteed value |
| --- | --- | --- | --- | --- |
| 2.8.1 | Electrical output transferred form the EVO outlet to the 35 kV distribution network (net) without heat delivery to the hot water piping system (state 1) | MWe | - | ≥ … (to be completed by the Participant) |
| 2.8.2 | Electrical output at the terminals of the turbo generator (gross) in EVO operation without heat delivery to the hot water piping system (state 1) | MWe | - | ≥ … (to be completed by the Participant) |
| 2.8.3 | Electrical output transferred from the EVO outlet to the 35 kV distribution network (net) with 32.0 MWt of heat delivery to the hot water piping system (state 2) | MWe | - | ≥ … (to be completed by the Participant) |
| 2.8.4 | Electrical output at the turbo generator terminals (gross) in EVO operation with 32.0 MWt of heat delivery to the hot water piping system (state 2) | MWe | - | ≥ … (to be completed by the Participant) |
| 2.8.5 | Rated stable thermal output for heat delivery to the hot water piping system (while concurrently achieving guaranteed parameter 2.8.3) | MWt | ≥ 32 | ≥ … (to be completed by the Participant) |
| 2.8.6 | Gross electrical efficiency in maximum condensing operation of the turbo generator (state 1) | % | ≥ 25 | ≥ … (to be completed by the Participant) |

The Participant shall prepare thermal balance charts for the above-mentioned operating modes and attach them as Annex 1 of this Enclosure 2 of the contract.

## Vacuum drop

(Test) proving conditions:

The input conditions according to Chapter 1 shall apply.

The vacuum drop shall be below the stipulated value in all TG operating states.

Guaranteed value:

| Parameter |  | Unit | Limit value |
| --- | --- | --- | --- |
| 2.9.1 | Vacuum drop | Pa/min. | ≤ 400 |

## Service life of boiler components

Maximum wear of materials – service life

Provide the work is operated in accordance with the operating conditions per the contract, the following maximum allowed wear and tear will be permitted during the warranty period specified in the contract (Art. 45.1.1.1 ii) to iv)) :

| Parameter |  | Warranty period | Guaranteed value |
| --- | --- | --- | --- |
| 2.10.1 | Maximum boiler grate wear = maximum % of grate bars replaced by the contractor due to ordinary wear and tear, in relation to the total amount of grate bars installed (including dividing and fixed bars). A grate bar assigned to be replaced is deemed such a grate bar which has been damaged (by heat, mechanically or in any other way, i.e. perforated, twisted, broken etc.), to the extent, it’s no longer able to fulfil its function. | … To be completed by the Participant per the contract, Art. 45.1.1.1 ii) | … %/year To be completed by the Participant (max. 5 %/year) |
| 2.10.2 | Maximum boiler lining wear – tiles (i.e. SIC panels). A damaged tile is deemed especially (but without limitation to) a tile which has fallen off or is no longer in its original position or is broken on more than ½ of its dimension or evinces an abrasive wear with loss of material in its entire thickness or other damage reducing the boiler lifetime. | … To be completed by the Participant per the contract, Art. 45.1.1.1 iii) | … m2/year To be completed by the Participant, max. 2.5%/year of the total area, at the same time the maximum extent of a single contiguous damaged area must not exceed 0.8 m2 |
| 2.10.3 | Maximum wear of the refractory concrete (or of another similar material with the same function) reducing the boiler lifetime. | … To be completed by the Participant per the contract, Art. 45.1.1.1 iii) | … m2/year To be completed by the Participant, max. 2.5%/year of the total area, at the same time the maximum extent of a single contiguous damaged area must not exceed 1.0 m2 |
| 2.10.4 | Abrasive and / or corrosion loss of the original thickness of theanti-corrosion alloy cladding of the outlet superheater | … To be completed by the Participant per the contract, Art. 45.1.1.1 iv) | … %/year To be completed by the Participant |
| 2.10.5 | Abrasive and / or corrosion loss of the original thickness of theanti-corrosion alloy cladding outside of the outlet superheater | … To be completed by the Participant per the contract, Art. 45.1.1.1 iii) | … %/year To be completed by the Participant |
| 2.10.6 | Abrasive and / or corrosion loss of any part of the boiler pressure unit other than parts protected by anti-corrosion alloy cladding | 24 months | … %/year To be completed by the Participant, max. 2.5 %/year |
| 2.10.7 | Abrasive or corrosive loss on any part of the flue gas transportation and treatment unit (vents, filters, flaps,...) | 24 months | … %/year To be completed by the Participant, max. 2.5%/year of the original thickness of the wall per the documentation |

The values specified according to 2.10.1 to 2.10.3 constitute total quantities (accumulated) which may be repaired / replaced on an annual basis during the warranty period and relate to the total quantity (area) regardless of their location.

The values specified according to 2.10.4 to 2.10.7 only apply to the single most damaged location.

Maintenance works including a visual and non-destructive inspection are supposed to be carried out during regular shut-downs. In the case of a repeated damage of repaired places, such damages are counted again into the total accumulated amount, which has to be repaired.

## Availability of the work

The availability of the Work is the undertaking of the contractor based on the combination of capacity availability of steam production by firing waste in accordance with the contractual terms and conditions and the Availability of the steam-water cycle for the provision of guaranteed output in the form of electricity and heat.

Guaranteed value:

| Parameter |  | Unit | Limit value | Guaranteed value |
| --- | --- | --- | --- | --- |
| 2.11.1 | Annual capacity availability of steam production [VDP] from firing fuel according to the contract | GWh | 95% of guaranteed value | ≥ … To be completed by the Participant* |
|  | Mass flow rate of steam at the temperature and pressure of the output steam according to chapter 2.6 | kg/s |  | ≥ … To be completed by the Participant* |
| 2.11.2 | Availability of operation (steam production) | h/year | 8,000 | ≥ … To be completed by the Participant |
| 2.11.3 | Availability of steam-water cycle (VWSC) | h/year | 8,580 | ≥ … To be completed by the Participant |

- * The calculation will be performed by the participant for the tender phase in such a way that the annual power availability of steam production corresponds to the amount of superheated steam from the boiler multiplied by the enthalpy of superheated steam from the boiler for the parameters according to chapter 2.6 and the designed hours according to parameter 2.11.2

### Annual capacity availability of steam production [VDP ]

The annual capacity availability of steam production [VDP] is recorded and documented as the sum of hourly mean values of heat produced in the boiler in the form of produced steam per hour via the installed operating measuring equipment for a time of 8,760 h a year.

The annual capacity availability of steam production [VDP] is calculated as the sum of all relevant registered hourly mean values and is stated in gigawatt hours [GWh]:

VDP = ∑(mNVi x (hVPi - hNVi) + mODi x (hODi – hVPi) )/106

where:

i:	Time interval 1 - 8,760 h a year

mNVi: 	The quantity of feeding water [kg/s] is the average for a time interval of one hour in which steam is produced according to the reference variables of the target steam temperature and steam pressure.

mODi:	The quantity of sludge/blowdown [kg/s] is the average for a time interval of one hour in which the boiler desludges/blows down.

hNVi:	The enthalpy of feeding water (calculated according to IAPWS-IF97) in [kJ/kg] is the average within a time interval of one hour ascertained from the feeding water temperature [°C] and the feeding water pressure [bar(a)] when measuring the quantity of feeding water.

hODi:	The enthalpy of sludge/blowdown (calculated according to IAPWS-IF97) in [kJ/kg] is the average within a time interval of one hour ascertained from the sludge/blowdown temperature [°C] and the sludge/blowdown pressure [bar(a)] when measuring the quantity of sludge/blowdown.

hVPi  : 	The enthalpy of output steam (calculated according to IAPWS-IF97) in [kJ/kg] is the average within a time interval of one hour ascertained from the steam temperature [°C] and the steam pressure [bar(a)] when measuring the quantity of steam.

Under operating conditions in which the target mass flow rate of steam is not achieved for reasons for which the contractor is not responsible, the contractor shall receive for the relevant time interval offset of 100% performance of the contract with regard to the guarantee of availability of steam production according to the definition. This stands for operation states in which the net calorific value is lower than 10 Mj/kg, determined online by determining the net calorific value, but the flow rate of fuel is equal to or greater than the ensured flow rate of fuel at load point “D” of the capacity diagram and for operation states when the purchaser is unable to ensure waste to a sufficient quantity and for the requirements of the purchaser on the partial load of the work.

### Availability of operation (steam production)

The availability of operation means the relative time for which the work is able to operate in the entire range of the firing capacity diagram of the boiler while meeting the requirements for operation according to Chapter 5.3.1 of Enclosure 1, i.e. the period during which the work is either working or is ready for immediate start [hours].

(Test) proving conditions:

The availability shall be evaluated by the Purchaser at participation of the Contractor on the basis of the operation records of the facility for the given year,

Availability  includes the time for start-up from downtime and downtime:

caused by external influences or by force majeure,

caused by incorrect service (failure to observe the operating instructions),

caused by a failure of the plant out of the range of the work,

arising from decisions or for a reason on the Purchaser’s side.

### Availability of steam-water cycle (VWSC)

The availability of the steam-water cycle is when waste is thermally converted into the target mass flow rate of steam and this target mass flow rate of steam is fully used through the steam turbine, in accordance with the Purchaser’s capacity requirement, for the generation of electricity and heat for district heating and these are fed into the relevant external networks.

The period of availability of the steam-water cycle [VWSC] is the time period during which the defined parts and components of the facility which generate electricity and heat for district heating are operational in accordance with the contract or are ready to generate electricity and heat for district heating. During a time of readiness for operation, it is expected that the WSC status (ready/not ready) of the facility will be the same as before its start in the case that these operation states are caused by restrictions to other facilities apart from WSC which are within the contractor’s sphere of performance. The period of readiness is determined using the sum of the evaluated operating time and the time of readiness for operation.

The facility according to WSC includes all parts of the facility and components of the steam-water cycle (water-steam), the system of feeding the boiler with feeding water, the steam turbine with condensation, cooling and exchange station, including the generator and electricity installation through the generator transformer, compressor station, etc.  These are all main aggregates for the generation of electricity and district heat with accessories and auxiliary facilities to the extent of the work, save the facilities listed in PS 01 Waste processing technology and its directly related accessories (hereinafter referred to as WSC).

In operation states when the required need for district heating cannot be satisfied or can only be partly satisfied on account of limitation of performance on the part of the contractor, the reduced capacity is determined by factor [FAWSC] and the operational time is shortened proportionately.

- The time of availability of the steam-water cycle [VWSC] is recorded as the hourly average during the period of availability, calculated as follows and stated in hours [h]:

VWSC = ∑(TB, i-WSC x FAWSC,i + T BR, i x FAWSC,i )

i:	Time interval 1 - 8,760 h a year

TB, i-WSC: 	is the time interval [h] in which all WSC facilities are in operation according to the purchaser’s load requirement. The startup and shutdown times are not included.

FAWSC,i : 	is the factor calculated as the ratio actual supply of district heating [FWrec,i ] to the target supply of district heating [FWexp,i]. The factor is evaluated as FAWSC,i = 1 for each time interval in which the target supply of district heating = 0 MWh.

FAWSC,i = FWrec,i / FWexp,i

TBR, i : 	is the time interval of readiness for operation [h] in which the defined components of the facility are ready for operation, but cannot be operated for reasons outside the control of the contractor.

## Uninterrupted boiler operation time

The term “uninterrupted boiler operation time” means the time between two planned inspection shut-downs for which the boiler, can be operated at the maximum fuel heat capacity without the flue gas temperature at the boiler outlet (230°C) being exceeded.

(Test) proving conditions:

The input conditions according to Chapter 1 shall apply,

Interruption of the uninterrupted boiler operation time is specified as a state during which it is necessary to shut down the boiler as a result of the fouling of the heat transfer surfaces.

During such time, a forced shut down for reasons other than to remove fouling from the heat transfer surfaces will be accepted (however, cleaning of the heat transfer surfaces is not permitted during such shut-down)

The uninterrupted boiler operation time shall be evaluated by the Purchaser at participation of the Contractor on the basis of the operation records of the plant for the entire time of the warranty period.

Guaranteed value:

| Parameter |  | Unit | Limit value | Guaranteed value |
| --- | --- | --- | --- | --- |
| 2.12.1 | Uninterrupted boiler operation time | hours | ≥ 8,000 | ≥ … To be completed by the Participant |

## Noisiness

The levels of noise exposure shall not exceed the maximum hygienic limits stipulated primarily by Act 258/200 Coll., on Public Health Protection, as amended, and Government Regulation 272/2011 Coll., on health protection against harmful impact of noise and vibrations, as amended.

Exceeding noise limits may be grounds for non-acceptance of the work and/or for the withdrawal from the contract – see Art. 44.2.12 of the contract.

Limits for noise from stationary sources during EVO operation – protected outdoor area of buildings:

for day-time LAeq,8h = 50 dB(A) (for the most noisy 8 hours)

for night-time LAeq,1h = 40 dB(A) (for the most noisy hour)

These levels shall be verified in points determined by the approving public authorities.

Indoor environment:

Indoor areas which are not permanently occupied		max. 85 dB(A), 1 m from equipment
Internal roadways				max. 75 dB(A)
Control room						max. 50 dB(A)
Offices, laboratories				max. 60 dB(A)

# Guarantee measurement conditions

The guarantee measurement conditions shall be drawn up at a detailed level by the contractor in the guarantee measurement design – see Chapter 2.11 of Enclosure 3 of the contract.

- The guaranteed values according to Chapters 2.1 to 2.9 and Chapter 2.13 shall be verified within the scope of test “A” and test “B”.

- The guaranteed values pursuant to Chapter 2.10 (wear and tear), evaluated annually during regular boiler shut-downs, will be verified during the warranty period.

The guaranteed values according to Chapter 2.11 and 2.12 shall be evaluated on the basis of a long-term operation records and shall be evaluated in each year of the warranty period.