Enclosure 3

DoCumentaTION

The below stated Enclosure 3 – Documentation shall be filled in / completed by the Contractor / Participant and submitted in File C3 of the indicative tender / tender (as an Enclosure to the Draft contract for Work) in accordance with instructions of the Contracting Entity concerning the preparing of File C3, included in Part 4 of the Tender Documentation.

Enclosure 3 states the purchaser’s requirements for the scope and preparation of the documentation to be drawn up by the contractor within the framework of the implementation of the Work, manner of its marking, approval by the purchaser and other requirements for its implementation and handling thereof.

TABLE OF CONTENTS

1.	Purpose of the documentation drawn up within the framework of the CONTRACT	5

2.	Documentation drawn up within the framework of the CONTRACT	6

2.1	Rules of administrative procedure	7

2.2	Time schedule of the documentation creation (PLTD)	8

2.3	Documentation for quality assurance	9

2.3.1	Quality Plan	9

2.3.2	Inspection and Test Plan	9

2.3.3	Test programmes	10

2.3.4	Inspection and Test Book	11

2.4	Site facilities design	11

2.5	Documentation for execution of the project (DESIGN)	12

2.5.1	Phases of the Documentation for execution of the project	12

2.5.2	Scope and content of documentation for execution of the project	14

2.5.3	Specific requirements of the Purchaser for Documentation for execution of the project	15

2.5.3.1	Documentation of the comprehensive solution of the Work	15

2.5.3.2	Documentation of operational wholes / process systems	15

2.5.3.3	Documents	16

2.5.3.4	Register of KKS marking	16

2.5.3.5	List of spare parts and fast wearing parts for two-year after-warranty operation	16

2.6	Documentation to application for a change in the construction before its completion	17

2.7	Update of principles of the construction organisation (ZOV)	17

2.8	OHS Plan	18

2.9	Accompanying technical documentation	18

2.10	Design for the first commissioning	19

2.11	Design for the guarantee measurement	20

2.12	Operation regulations	21

2.13	Regulations for maintenance	22

2.14	Documents for permission of the trial operation and obtaining of the final approval to use	22

2.15	Documentation for training of the Purchaser’s staff	23

2.16	As-built documentation of the Work	23

3.	Quantity, form and language of the documentation drawn up BY the Contractor	24

3.1	Quantity of documentation	24

3.2	Documentation form	25

3.2.1	Printed form	25

3.2.2	Electronic form	25

3.2.2.1	Format of files	25

3.2.2.2	Organization of electronic documents on DIGITAL media	26

3.3	Language of the documentation	26

4.	Coding	27

5.	Approval of the documentation	27

6.	Data to be handed over by the Purchaser	28

7.	Documentation handover deadlines	29

# Purpose of the documentation drawn up within the framework of the CONTRACT

The Documentation drawn up within the framework of the Contract must be delivered by the Contractor in such an extent, quantity, deadlines and quality that it can facilitate:

obtaining of all permissions, consents and opinions of state administration bodies, which are according to applicable legislation necessary for implementation and operation of the Work,

assessment of the general design of the Work, its division into time sections in accordance with the time plan and assessment of its conformity with the requirements of the Contract and conclusions or requirements of the legislative proceedings concerning the construction,

coordination of the Work with other activities on the site,

assurance of quality of the Work,

implementation of the Work, its erection and putting into operation,

implementation of the guarantee measurement,

training of the Purchaser’s staff,

operation, maintenance and repairs of the Work,

documenting of the final condition of the Work.

For the entire term of implementation of the Work, the Contractor shall maintain a database (list) of the documentation handed over. This database shall be processed in a computer form according to Chapter 3 below and shall include at least the following data:

document / drawing number,

document / drawing name,

date of issue and number of the latest valid revision,

document / drawing status, in accordance with the approval procedure,

date of approval for approved documents,

author of the document,

type of documentation (Documentation for execution of the project, Documentation for quality assurance, Documentation for site facilities, etc.).

The current version of the database in an electronic version will be handed over to the Purchaser together with each documentation handed over (even a part or revision of the documentation).

# Documentation drawn up within the framework of the CONTRACT

Within the framework of the Contract, the Contractor shall deliver moreover at least the below specified documentation:

Rules of administrative procedure

Time schedule of the documentation creation (PLTD)

Documentation for quality assurance

Site facilities design

Documentation for execution of the project (design)

Documentation to application for a change in the construction before its completion

Principles of the construction organisation (ZOV)

Occupational Health and Safety (OHS) Plan

Accompanying technical documentation

Design for the first commissioning

Design for the guarantee measurement

Operation regulations

Regulations for maintenance

Documents for permission of the trial operation and obtaining of the final approval to use

Documentation for training of the Purchaser’s staff

As-built documentation of the Work

All of this in the arrangement and forms as required in the text below of the present Enclosure. It being understood that the text includes detailed requirements only for those types of the documentation which is not described at a detailed level in other parts of the Contract (e.g. time schedules).

All the documentation handed over by the Contractor shall be drawn up in a clear and readable form and in accordance with standards and good engineering practices.

## Rules of administrative procedure

The Rules of administrative procedure (AŘ) specify binding rules for communication between the Contractor and the Purchaser and the rules for the handling of written documents drawn up within the framework of implementation of the Work.

This document specifies procedures for the exchange of written materials between the Contractor and the Purchaser, issuing, distribution, revisions and archiving of written materials.

It determines also the rules for electronic communication between the Purchaser’s representative and the Contractor’s representative.

The Rules of administrative procedure shall include, without limitation to:

- Introductory data

- Purpose and validity of the document

- Definitions and abbreviations

- Determination of input and output places (on the part of both the Contractor and Purchaser)

- Rules of mutual communication and correspondence procedures, outlining of responsibilities

- Marking of the correspondence (both hardcopy and electronic correspondence)

- Addresses, identification, responsible (contact) persons and connection to the Purchaser, Contractor, Project Manager (Technical Supervision of the Investor - TDI), Authorised Person, Notified Person, OHS Coordinator, independent contractor of the guarantee measurement and Purchaser’s consultants

- Publicity of the Work

- Final provisions

Annexes, such as:

Name organisational chart of the Contractor for implementation of the Work

Name organisational chart of the Purchaser for implementation of the Work

etc.

## Time schedule of the documentation creation (PLTD)

The Time schedule of the documentation creation shall describe the way and procedures of the creation of the Contractor’s documentation drawn up within the framework of the Work, shall specify the documentation approval programme and shall determine the deadlines of the presupposed issue of individual documents.

It shall contain in particular:

1)	Formal rules for creation of the documentation, such as:

SW tools used,

uniform identification system of the printed documentation,

manner of identification of electronic files,

rules for identification of the documentation of subcontractors,

specimens of the stamps used on the drawings,

templates of title and other pages of written documents,

templates of letters, reports, forms, minutes, reports, change sheet (order),

method distribution management and storage of documentation, incl. marking of revisions,

change management.

2)	List of documentation drawn up by the Contractor in the extent provided for in Chapters 2.3 to 2.16 of the present Enclosure 3 to the Contract, from which at least the following details shall be clear for each type of the document:

framework content and structure of the document,

author of the document (Contractor or its subcontractor),

for database documents (lists), the database structure will be stated.

For documents which are to form a part of the Design it will be specified which information is to be included in phase 1 of the Design and which in phase 2 of the Design (see Chapter 2.5.1).

3)	Time schedule of approval and handover of the documentation, according to which the Contractor will submit to the Purchaser, on a gradual basis for approval, individual parts of the documentation, including, without limitation to:

presupposed deadlines of consultations between the Contractor and the Purchaser,

planned deadlines of objections and approvals of documents by the Purchaser,

possibly other data necessary for management and coordination of creation of the Contractor’s documentation, such as the necessary inputs of subcontractors and their deadlines.

The time data will be based on the applicable version of the time and implementing schedules.

The current version of the programme approval and handover of documentation shall always be submitted as one of the grounds for progress meetings according to Art. 20 Contract.

## Documentation for quality assurance

The quality assurance documentation shall include:

Quality Plan

Inspection and Test Plan

Test programmes

Inspection and Test Book

### Quality Plan

The Work Quality Plan must be drawn up by the Contractor in accordance with ČSN ISO 10005.

The Quality Plan shall be drawn up for the entire extent of the Work and must include a quality management procedure for all activities within the framework of the Work implementation.

The Quality Plan shall state a list of individual activities affecting the quality of the Work.

It will specify responsibility, rights and obligations of staff members entrusted with quality management. Through its implementation it must demonstrate that the requirements specified in the Contract are planned and managed and that their development will be monitored. It will further determine the type of the standards used, technical conditions and regulations for implementation of inspections, types of quality records, who performs the tests and participation at these tests.

The Quality Plan shall clearly state how these activities are ensured in individual implementation phases, i.e. especially at:

designing (design solution),

business assurance of purchase of materials and subdeliveries,

company’s own production,

building work and assembly,

Commissioning,

trial operation.

### Inspection and Test Plan

The Contractor shall draw up the Inspection and Test Plan (PKZ) which is to include all inspections and tests carried out by the Contractor and its subcontractor. The extent of the tests is provided for in Chapter of 10 Enclosure 1 to the Contract (Purchaser’s requirements for technical design of the Work) for all the phases of preparation and implementation of the Work, through which it shall ensure and prove the conformity of the Work with the Purchaser’s requirements.

This concerns especially:

inspections and tests during acceptance of materials and subdeliveries of devices produced in a mass production system,

inspections and tests during production of individually produced equipment,

inspections and tests of finished products (Factory Acceptance Test – FAT),

inspections and tests of the building part,

inspections and tests during acceptance of erection equipment,

individual tests (IZ) within the framework of the erection completion,

inspections and tests during Commissioning, which are to include:

preparation for complex tests,

complex tests, including Test “A”,

performance test,

test “B”.

The Inspection and Test Plans drawn up for individual SO/IO/PS and arranged in a time sequence of their implementation, they shall include especially:

name of the test or inspection,

the equipment tested or checked,

type of the tests (classification from the viewpoint of the above mentioned types of inspections and tests),

technically clear specification of a particular inspection or test,

inspection methods and regulations for its implementation (inspection procedure), including criteria for evaluation of the inspection or test results. In the case of inspections or tests for which also the programme of tests is drawn up in accordance with Chapter 2.3.3, the criteria for evaluation of the results of inspections or tests can only be stated at a more detailed level in the follow-up programme of the tests,

method of recording of the result (finding) of the inspection, test and their evaluation,

place for recording of witness (W) or hold (H) points of the customer inspection of the Purchaser, or of an independent third party entrusted therewith.

For individual inspections and tests it is necessary to mark for which tests the Contractor is obliged to invite the Purchaser’s representative.

### Test programmes

Test programmes will be drawn up only for:

inspections and tests carried out within the framework of FAT

inspections and tests at Commissioning

inspections and tests carried out at test “B”.

The Test programmes shall include especially:

target of the test,

values which are to be proven and parameters which are to be achieved,

description of preparation and test procedure including the time schedule of the test as well,

list of inspected and tested equipment or its parts or the whole,

requirements for preparedness of functionally related equipment,

requirements for the staff for implementation tests (including the Purchaser’s staff where their assistance is necessary),

bar chart with the marking of individual activities,

list of documents and valid standards, according to which the test or inspection is to be carried out,

methodology of measurement and method of evaluation,

successfulness criteria,

list of all instruments used at tests or inspections and reports on their calibration,

draft partial reports evaluating the course of the test or inspection (if any),

draft final report for the test or inspection.

The extent, implementation and quality of the tests or inspections must correspond at least to the requirements of the Contract and to the requirements stated in the applicable standard for the equipment in question.

Note:

The programmes of inspections and tests for FAT shall include only those data from the above mentioned list which are relevant for this type of test (without a link to the technology and staff of the Purchaser).

### Inspection and Test Book

The Inspection and Test Book shall include an integrated file of documents (reports) with the results of all performed inspections, tests, acceptances and tests according to PKZ. It will include also the copies of calibration reports of the instruments used.

The documentary part of the inspections and tests shall be conducted separately for the building part, machinery-technological part, electrical equipment and I&C (I&C system) in separate files and in the course of implementation of the Work it will be completed on a gradual basis.

## Site facilities design

The site facilities design shall include solutions for:

unloading places for deliveries,

pre-assembly and erection areas and their mechanisation,

energy sources and their distribution on the site,

storage facilities and storage areas,

social and technical conditions,

use of assembly mechanisms and methods of their application,

connection places to the existing equipment,

illumination,

fencing and method of safeguarding.

The Design will include also the layout drawing of the site facilities.

The drawing shall be drawn up at a scale of 1:500 and shall include especially:

position and height marking of all existing buried utilities and other covered facilities,

marking of the circumference of the construction and of the temporary circumference of the site out of the construction area,

position and height marking of the proposed construction, including its connection to the existing facilities of the Purchaser, possible realignments of buried or overhead distribution networks,

areas in which it is possible to build up landfill facilities and temporary constructions of site facilities,

entrances and vehicle entries to the main and side sites,

marking of water and energy inlets to the site, including offtake places, place of connection of the sewerage system from the constructions of site facilities, drainage, telephone connection.

## Documentation for execution of the project (DESIGN)

Documentation for execution of the project (hereinafter referred to also as the Design) is the documentation within the meaning of the Act no. 183/2006 Coll. (Building Act) and Annex no. 13 to the Regulation no. 499/2006 Coll. (on construction documentation).

The Design will further develop the Design Documentation for Building Permit and will take into consideration all the conditions and requirements for construction issued by the Building Authority and other concerned state administration bodies and concerned persons and entities, as well as conditions of the planning permission, EIA and IPPC (the Design Documentation for Building Permit was processed by an external organisation of the Purchaser and is part of Enclosure 1 as Appendix D01.

The Design shall include all the information and documentation necessary for implementation of the Work, including the data and details of the technical solution, conditions for implementation and links to the existing or new facilities of the Purchaser.

For the purpose of documenting the design of the Work as a whole and for its coordination, the Design will be completed, beyond the framework of requirements of the Regulation no. 499/2006 Coll., with a separate file containing the Comprehensive Solution of the Work in all the professions.

The grounds for the drawing up of the design shall be especially:

contract, including all its Annexes,

Design Documentation for Building Permit, including conclusions, objections and requirements of concerned entities and persons,

valid methodology of marking of the facilities by means of the KKS system,

changes required by the Purchaser arising in the course of preparation of the design.

The Design shall be drawn up as an integrated uniformly drawn up whole from the Contractor – it shall consistently include also the data and documentation from individual subcontractors.

### Phases of the Documentation for execution of the project

The Design shall be formed by the set of the documents defined in advance which are to be gradually developed, clarified or complemented depending on the needs of the given phase of preparation and implementation of the Work. The documentation shall be handed over on a gradual basis in several phases and each phase will contain those documents from the above mentioned set of documents (or their revision) which correspond, in terms of the content and rate of details, to the purpose of the phase in question.

The following phases of creation and gradual handover of the Design are presupposed:

| Design Phase | Purpose of the documentation |
| --- | --- |
| Phase 1 (Basic Design) | Basic Design Solution of the Work and of the procedure of its implementation shall serve especially for: verification of conformity in terms of the extent and solution of the Work with the Contract, technical standards, applicable law regulations and OSS decisions, preparation of the Design and implementation of the Work, coordination of the Work, both internal (towards the subcontractors), as well as external. Phase 1 of the Design shall include: documentation of a comprehensive solution of the Work, describing the solution of the Work as a whole, basic design documentation for all building structures (SO), infrastructure units (IO) and process systems (PS), and will be drawn up at the detail level necessary for fulfilment of the purpose of phase 1 of the Design. |
| Phase 2 (Detail Design) | The detailed design documentation for implementation of the Work shall serve especially for: implementation of the Work on the site, performing the work implementation supervision by the purchaser and by the project manager, submission to state administration bodies in the cases provided for in the Building Permit or where required by law regulations of the Czech Republic. Phase 2 of the Design shall include the documentation in progress drawn up in phase 1, i.e.: updated and completed documentation of the comprehensive solution of the Work, detailed design documentation of building structures (SO), infrastructure units (IO) and process systems (PS). The output from this phase will be the complete documentation for execution of the project (Work) with all the necessary details, which is to correspond to all the below stated requirements for its scope and content. The documentation issued in phase 2 will take into consideration all the Purchaser’s objections relating to phase 1. |
| Phase 3 (As Built) | As-built documentation for execution of the Work after completion of its implementation (revised documentation from phase 2 – see Chapter 2.16 for detail). Within the scope of the phase 3, the contractor shall provide as-built documentation of the Work which shall contain all the changes arising in the course of construction, erection and Commissioning and trial operation (changes of the completed work against the approved documentation, phase 2). |

### Scope and content of documentation for execution of the project

The Design shall include, for all the phases of preparation:

Documentation of the comprehensive solution of the Work

The documentation shall be drawn up as a separate file for the Work (project) as a whole and shall furthermore be divided into several parts: construction part, machinery-technological part, I&Cpart and operational distribution system of heavy current.

Design documentation with basic arrangement into the following sections:

A. Documentation of construction building structures (SO)
with arrangement into individual construction building structures

B. Documentation of infrastructure units (IO)
with arrangement into individual infrastructure units

C. Documentation of process systems (PC / PS) including:

C.1	Machinery and technological facilities
with arrangement into operation wholes and further into process systems where relevant.

C.2	I&C 
with arrangement into:

comprehensive technical report,

HW documentation,

application SW documentation including source codes,

field instrumentation and cabling system.

C.3	Electrotechnical facilities
with arrangement into operation wholes and further into process systems where relevant.

Accessories including:

Documents

Register of KKS marking

List of spare parts and parts which are subject to fast wear and tear for a two-year warranty operation

The Contractor shall propose a detailed extent and content of the Design and while doing so, it is necessary to meet:

the requirements stated in Annex no. 13 to the Regulation no. 499/2006 Coll. on documentation of constructions,

below stated specific requirements of the Purchaser.

The agenda of individual chapters and subchapters of the Design shall correspond to the actual extent of the Work, i.e. it shall not take into consideration those requirements stated in Annex no. 13 to Regulation no. 499/2006 Coll. on documentation of constructions, which do not have any relevance to the Work implemented.

### Specific requirements of the Purchaser for Documentation for execution of the project

#### Documentation of the comprehensive solution of the Work

The documentation of the comprehensive solution of the Work shall include technical report, drawing, computations and lists documenting concepts of the construction as a whole in all professions, including all links among individual SO, IO and PS, and all other documents and databases necessary for coordination of the Work as a whole – both internal (between the individual SO, IO and PS Work) and external (between the Work and follow-up constructions and facilities).

This concerns especially:

the concept of the Work in all professions, parameters of the Work, technology used, arrangement into individual IO, SO, PS, incl.:

layout design of the Work as a whole,

design of interiors of office buildings

design of the interior and exterior information system and design of advertisements and markings

technological design of the Work as a whole, including all related calculations, technological and balance charts, general coordinated lists, etc.,

I&C design of the Work as a whole, regardless of the fact whether individual elements of the system are included in technological PS – general configuration chart, communication methods used, manner of solution of links to electrical facilities, technology control concepts, arrangement of control rooms and deployment of elements for contacts with operators, coordinated lists of measurement and signals, etc.

design of electrical equipment of the Work as a whole, regardless of the fact whether individual elements of the electrical systems are included in technological PS.

#### Documentation of operational wholes / process systems

The design documentation of operational wholes / process systems (i.e. part C of the Design) shall include, beyond the framework requested in Annex no. 13 to Regulation no. 499/2006 Coll. on documentation of constructions, especially:

In the technical report:

possible deviations of the Design compared to the verified design documentation for building permit,

compliance with the conditions specified in the Building Permit,

list of applicable standards used - ČSN, ČSN EN and IEC or other standards.

In the drawing part:

The drawing part of the process systems shall include, depending on the purpose of the concerned operation whole / process system, technological charts, layout drawings of individual facilities (machinery, electrical, as well as I&C), drawings of cable routes, dimensional drawings, single-pole wiring charts, grounding charts and charts for protection from electrical current, protection system charts, energising and phasing charts, drawings of internal and external connection for all terminal boards of all switchboards, cabinets and special equipment, P&I charts with marked measurement sites, general configuration chart of the control system, front designs of control panels/counters, drawings of workplace arrangement, I&C power supply chart, logical charts of the control system, line charts for connection, terminal charts, position descriptions, views of switchboards, drawings of throttling elements, cabling charts, constructional drawings, etc.

In the list part:

The lists shall include lists of machines and devices, lists of pipelines, valves and fittings, including regulation elements, lists of electrical appliances, lists of measurement circuits, lists of actuating elements, lists of inputs and outputs of the automation stations, cable lists, etc.

In the computational part:

The computations shall be drawn up in the necessary extent and in a checkable form.

The computations shall include computations of steel structures, pressure parts, balance computations, strength analyses, reliability computations, computations of regulation valves and throttling elements (curtain, nozzles), computations of production of waste heat, computations of voltage and short-circuit characteristics, computations of occupancy of cable routes, etc.

All parts of the documentation must be mutually interconnected by references for the purpose of an easy orientation in the documentation and effective work with the documentation.

The computations of steel structures, pressure devices, safety equipment etc. must be carried out by an authorised or notified person according to applicable legislation of the Czech Republic.

#### Documents

It is necessary to submit documents from the Design preparation, such as:

overview of map and geodetic background materials used,

documents arising in the process of creation of the Design (e.g. approved exceptions from ČSN, certificates of conformity, etc.),

list of reserved technical facilities,

records from consultations in the course of documentation preparation, possibly other documents arising in the process of Design preparation, etc.

Note: 
The documents shall form a part of the DOCUMENTATION FOR EXECUTION OF THE PROJECT – phase 2.

#### Register of KKS marking

The marking register shall include the list of all the KKS codes assigned, with the names of devices and with the number of technological drawings on which the device in question is stated.

Note: 
The register of KKS marking will be for the first time a part of the documentation for execution of the project – phase 1 and will be further updated and completed in phases 2 and 3.

#### List of spare parts and fast wearing parts for two-year after-warranty operation

The Contractor shall draw up a list of spare parts and fast-wearing parts for two-year after-warranty operation.

These spare parts and fast-wearing parts are not included in the contract price and the Purchaser reserves the right to order these spare parts at its discretion.

This list shall include all the information necessary for identification of spare parts and fast-wearing parts, including the frequency of replacement of fast-wearing parts, especially:

definition of spare parts (consumer material),

producer,

number of parts,

delivery term,

identification data (technical sheets),

frequency of change,

production documentation for fast-wearing parts that are not normally available on the market.

Note: 
The list of spare parts and fast-wearing parts for two-year after-warranty operation including manufacturing documentation for wearing parts that are not normally available on the market shall form a part of the documentation for execution of the project – phase 3 (As-built documentation for execution of the work).

## Documentation to application for a change in the construction before its completion

The Contractor shall draw up and provide to the Purchaser, after the drawing up of the documentation for execution of the project, all the documentation necessary for management of the application for a change in the construction before its completion and for legalisation of the construction resulting from differences of the implemented design solution from the design documentation for building proceedings (if there are such changes), possibly resulting from the Building Act (Act no. 183/2006 Coll.) and its implementing regulations (especially the Regulation no. 499/2006 Coll.).

The documentation shall be drawn up in two stages:

| Phase | Purpose of the documentation |
| --- | --- |
| Stage 1 | Documentation documenting changes arising in the course of preparation of the Design phase 1, which means between the solution of the Work and design documentation for building proceedings. |
| Stage 2 | Documentation documenting other possible changes arising in the course of preparation of the Design phase 2 and in the course of Commissioning, which means between the state of the Work and design documentation for building proceedings |

A part of the documentation in both the stages of preparation shall be also the revision of the Fire Safety Design of the Project (PBŘ), if it is requested by the changes carried out on the project.

## Update of principles of the construction organisation (ZOV)

The Contractor shall update the Principles of the construction organisation which will be based on the ZOV, reported within the documentation for the building permit and will be in accordance with the Time and implementation plan for the Work and shall be based on the particular terms and conditions given by the site, actual draft solution of the Work and proposed construction procedure.

This document shall deal with principal conditions for building up of the site facilities, project implementation, project impacts on the existing operation, surroundings and on the environment, protection of health of people, internal and external traffic solution associated with the project, land occupation and other possible elements affecting the procedure of the Work implementation.

The Principles of the construction organisation shall include without limitation to:

- General project description,

- Project arrangement,

- Supplier system,

- Principles of cooperation with the Purchaser at the Work implementation,

- Time and execution plan of implementation of the Work (current and detailed version of the Time and execution plan of implementation of the Work stated in Enclosure 4 to the Contract), which is to deal with activities on the site at a detailed level, including implementation of building structures, assembly of individual devices, activities carried out within the framework of the tests and Commissioning, assurance of links to the surroundings, use of assembly staff members, etc.

- Delivery assurance plan,

- Conditions for the marking of deliveries, packing, storage principles,

- Provisory elements,

- Winter measures,

- Environmental impacts of the Project,

- Methods of handling of waste,

- Occupational health and safety conditions.

A part of ZOV will be also the site facilities design – see Chapter and 2.4.

## OHS Plan

The Contractor shall draw up, according to requirements of the Act no. 309/2006 Coll., regulating other requirements of occupational health and safety in employment relations and on assurance of safety and health protection during activities or provision of services out of employment relations (Act on assurance of other conditions of occupational health and safety), the plan of occupational health and safety on the site, within the meaning of Government Regulation no. 591/2006 Coll., on more detailed minimum requirements for safety and health protection at work on sites.

The plan of occupational health and safety on the site shall describe assurance and principles of compliance and prevention of OHS during the project implementation.

The plan shall be based on particular conditions on the site, on particular technological procedures, types of work and activities, through which the Contractor achieves implementation and shall have a close interconnection with the document entitled “Principles of the construction organisation”.

The OHS plan shall include the Contractor’s obligation to inform the Purchaser about the use of work procedures or materials which may represent an increased risk for the Purchaser’s property or for health and life of natural persons, who may be affected by the Contractor’s activities with regard to physical, chemical or biological effects of these activities and materials used.

The Contractor will be obliged to submit to the Purchaser the information on physical or chemical or biological effects of the work procedure or the materials used in the extent corresponding to the state-of-the-art technology at the time of use of this procedure, including introduction of preventive measures for assurance of protection of health and lives of natural persons in the place of work.

In the case of use of chemical substances or chemical preparations featuring at least one dangerous property within the meaning of provisions of the Act no. 350/2011 Coll., on chemical substances and chemical mixtures, as amended, the Contractor will be obliged to hand over, before the work commencement, to the Purchaser’s representative (or to the OHS coordinator appointed, if any) the Safety Data Sheet in the Czech language.

## Accompanying technical documentation

The accompanying technical documentation necessary for transport, assembly, commissioning, operation, troubleshooting and safe operation shall be delivered for all the deliveries within the framework of the Work, including the building part.

The documentation shall include, without limitation to:

data for identification of the parts delivered (part lists),

storage requirements,

filled in and confirmed technical data sheets and other documents, whose documentation results for the Contractor from regulations and ordinances of state authorities and ČSN,

assembly documentation – available technological procedures of assembly and disassembly from manufacturers of equipment, including corresponding drawing documentation,

passports of all pressure cylinders,

passports of pumps,

passport of the generator and its accessories,

passport of the turbine,

passports of hoisting devices

technical conditions for delivery, assembly, erection and operation of equipment and facilities,

operating, repair and maintenance instructions for the equipment,

documentation on the materials used,

certificates, safety data sheets, quality documents and declarations of conformity in accordance with applicable law regulations specified by the Act no. 22/1997 Coll., on technical requirements for products, with all associated, later, change or implementing regulations, Acts or ordinances,

production wiring charts of electrical equipment installed (switchboards, counters, control boxes, etc.),

etc.

The above listed documentation shall be divided into separate files in arrangement by building structures, machinery technology, I&C and electrical installation equipment.

## Design for the first commissioning

The design for the first commissioning shall be drawn up for the period from erection completion for the first start-up, i.e. it shall include the period of preparation for complex tests, actual complex tests and performance test.

It will include functional tests, including their preparation and description of conditions, testing media, temporary measures and test procedure, together with the results required.

The design shall include, without limitation to:

specification of initial parameters of the equipment supplied, necessary for the first start-up,

update of the plan of inspections and tests of the equipment for the period from erection completion to complex tests and follow-up programmes of the tests,

special cleaning operations for the boiler pressure system and pipeline distribution systems – especially rinsing, blows-through, conservation etc.,

requirements for preparedness of the following parts:

building part,

follow-up technological equipment,

electrical installation equipment,

I&C,

description of preparation and procedure for the first start-up,

list of operational materials and energy necessary for the first start-up,

staff requirements for putting individual sets into operation,

bar chart with the marking of individual activities with time assessment and follow-up of individual disciplines (building, machinery, electrical installations, I&C),

programme of the tests during operation,

program of adjustment and process optimisation.

The design for the first commissioning for the period of preparation for complex tests shall be based on the implementation of appropriate individual tests and shall deal, in a logical sequence, gradual commissioning of individual functional wholes and process systems.

The design for the first commissioning for the period of complex tests shall deal, on a gradual basis, with verification of all parameters and EVO functions.

In this part of the project it is also necessary to resolve the method of implementation of tests “A” (tests carried out by the Contractor).

The design shall also specify, at a detailed level, requirements for cooperation of the Purchaser, including follow-up suppliers, while carrying out functional tests (energy, media, operation staff, etc.), in accordance with provisions of the Contract.

## Design for the guarantee measurement

The design for the guarantee measurement shall meet the requirement for implementation of guarantee measurements incl. applied conversions to guaranteed conditions, measurement uncertainties, etc. will be processed in accordance with applicable standards and will include guarantee measurement for measurement of all guaranteed parameters as specified in the Contract and in Enclosure 2 to the Contract (Guaranteed parameters).

The design for the guarantee measurement shall include, for measurement of individual guaranteed parameters, without limitation to:

list of tests and testing to be carried out, including specification of the test targets,

standards, according to which the evaluation is to be carried out,

methodology of measurement of the values guaranteed and method of evaluation,

description of the measurement methods used,

list of measurement instruments used, with specification of their precision classes and calibration curves,

list of measurement sites,

complete set of correction curves and of other correction backgrounds,

list of measurement sites, with the marking in charts,

manner of implementation of measurement and connection sites for guarantee measurement,

time schedule of the measurements and tests carried out.

The design for the guarantee measurement shall include also the drawing documentation including:

measurement site layout charts (marking in the charts) – in cooperation with the supplier of the guarantee measurement,

design implementation of sites for test sampling and their arrangement – in cooperation with the supplier of the guarantee measurement,

measurement structure chart.

The design for the guarantee measurement shall determine also requirements for staff assurance of the tests and requirements for cooperation of the Purchaser, including follow-up suppliers, while performing guarantee measurements (energies, media, operation staff, etc.) in accordance with provisions of the Contract.

The design for the guarantee measurement shall be drawn up separately for the test “a” and test “b”, i.e. it is necessary to respect the requirement for implementation of guarantee measurements of individual guaranteed parameters as specified in the Contract and in Enclosure no. 2 to the Contract (Guaranteed parameters).

Notes:

1) 	The actual guarantee measurement shall be carried out by an independent company or person authorised by the Purchaser (and paid for separately by the Purchaser).

2)	The Contractor shall closely cooperate with such a company or person while drawing up the Design for the guarantee measurement, for the purpose of preparation of a complete and materially correct document.

## Operation regulations

The operation regulations for the technology supplied as a whole, for operation wholes and process systems and for individual devices shall be drawn up in such a way that they can enable operators to safely manage operation in all normal operation conditions, and at the same time they must provide operators with sufficient information about what to do in extraordinary conditions. They will also include instructions for how to operate the technology in question as cost-effectively as possible.

Operating regulations will be developed in the MPP template used by the purchaser.

The operation regulations shall include, without limitation to:

definition of basic terns,

list of abbreviations,

brief technical description, marking of equipment, its technical parameters,

drawing documentation (charts and dimensional drawings),

links to other equipment,

permitted deviations of parameters for normal operation regimes,

limit values for extraordinary operation conditions,

limit values for failure conditions (setting of protections),

organisational work for operated equipment,

appointment of the staff responsible for operation, servicing and inspection of operated equipment,

handling on the equipment,

safety of the equipment and staff, protection of the environment (safety measures, fire protection measures, …),

preparation for operation:

monitoring of the technological operation,

preparation of pipeline routes and actuation elements, description of the initial state,

commissioning of locking, protections, signalling and automatic control systems,

list of all releasing and locking conditions for individual devices,

methods of start-up for:

cold start, including start-up after BO (ordinary repair) and GO (overhaul),

hot start,

commissioning (manually, automatically),

inspection during operation,

stopping (operational, emergency),

exact verbal description of algorithms of binary management and regulations,

acceptable ranges of regulated quantities,

evaluation of failure conditions, setting of limit values and control circuits.

operator’s HMI handbook for DCS operators

The operation regulations shall include also the separately processed “Lubrication Plan” for all EVO equipment broken down by the technological segments and stating equivalents of individual lubricants (periods of replenishment of lubricants and oil replacement, specifications of lubricants and oils - number of types of lubricants shall be as limited and unified as possible).

## Regulations for maintenance

The regulations for maintenance shall be drawn up in such a way that they can serve as a basic aid for maintenance and assurance of spare parts and for training of the operation staff.

The regulations for maintenance shall determine exact specifications of prescribed and recommended works for BO and GO, the so-called “Type distribution of works” and “Postponement plan”, including requirements for spare parts, and they shall include especially:

specification of main equipment necessary for maintenance,

accessibility and conditions of interchangeability of elements and nodes, including the use of lifting devices for repairs and maintenance of main equipment,

principles of technological procedures and conditions for carrying out of maintenance and repairs of main equipment,

description of preventive and corrective maintenance, drawings and charts necessary for maintenance of individual devices,

time schedules and regulations for regular revisions and maintenance of individual devices,

lists of replacement parts and fast-wearing parts, with specification of all data necessary for their orders, in the case of fast-wearing parts also with specification of recommended replacement cycles.

special assembly procedures for the carrying out of maintenance work,

troubleshooting instructions,

drawings with specification of areas, spaces and access routes for dismantling of the main equipment and its nodes, including specification of lay-by areas with the marking of load bearing capacities.

For the equipment which cannot be repaired without stopping or reduction of output of the facility, the regulation for maintenance shall include an overview of all the parts with specification of their lifetime in relation to intervals of the repairs planned – BO, GO.

With regard to the fact that within the framework of the I&C maintenance, also the maintenance of servo-drives, shut-off fittings and related electrical installations is ensured, the stated documentation shall be drawn up, in the part of electrical installation equipment, in such a manner that it can be possible to work with it separately from the general documentation of electrical equipment. Also the operation regulations and documentation for maintenance shall be drawn up separately for this part.

## Documents for permission of the trial operation and obtaining of the final approval to use

The Contractor shall ensure, collect (if they are parts of documentary sections of other types of documentation) and hand over to the Purchaser all the documents necessary for obtaining of commencement of the trial operation on the part of the Building Authority and for obtaining of the final approval to use – except for those whose obtaining, assurance and documenting is imposed and determined by the Building Authority exclusively on the Purchaser (builder) in the Decision about the building permission.

Besides this, the Contractor shall provide all other documents which are requested by concerned state administration authorities during local investigations (before commencement of the trial operation and during final-approval-to-use proceedings) or on the basis of their additional requirements.

## Documentation for training of the Purchaser’s staff

The Purchaser shall receive from the Contractor all training materials in the Czech language. The extent of this documentation is stated in Enclosure 8 to the Contract.

For the training of operators it is necessary to ensure, sufficiently in advance, documentation for operators (HMI operating instructions) and regulation for equipment operation and maintenance.

## As-built documentation of the Work

After the commissioning of the Work and during the trial operation, the Contractor shall draw up and submit to the Purchaser the As-built documentation of the Work in the extent according to the Appendix 3 of the Regulation 499/2006 Coll.

This is the DOCUMENTATION FOR EXECUTION OF THE PROJECT (Design) - phase 3, as stated in Chapter 2.5.1 above.

Manner of issuing of the As-built documentation of the Work

One (1) complete set of the As-built documentation (phase 3) with the changes against phase 2 of the Design shall be handed over by the Contractor to the Purchaser (with the signing of a report) before the signing of the PAC. This documentation shall include all changes arising as of that deadline. Each document will be provided with the statement "The documentation corresponds to the actual execution of the work" with the date, the imprint of the company's business stamp and the signature of the contractor's representative. This documentation will also include a Geometric Plan focusing on all underground and above-ground networks and buildings (roads and buildings). The Geometric plan will be processed to enable the registration of buildings in the real estate cadastre. The handover of that documentation is a precondition for the signing of PAC by the Purchaser.

Ten (10) complete sets of clean copies of the As-built documentation of the Work, including also all changes arising in the course of the trial operation, including the source sets of documents drawn up for SW products, shall be handed over by the Contractor to the Purchaser (with the signing of a report) after completion of the trial operation. Each document will be provided with the declaration stating that “The documentation corresponds to the As-built implementation of the Work” with connection of the data, imprint of the commercial seal of the firm and signature of the Contractor’s representative.

The As-built documentation for execution of the Work will also include the SW documentation of all parts of the control systems, including their source codes.

This documentation shall include also an updated List of replacement (spare) parts and of fast-wearing parts for two-year post-warranty operation.

# Quantity, form and language of the documentation drawn up BY the Contractor

The documentation shall be drawn up in a uniform and comprehensible form and in accordance with good engineering practices. In the case of documentation ensured by a subcontractor, the Contractor shall ensure unification of the form and marking of the documentation within the framework of the entire Work.

All documents handed over by the contractor will be provided with a title stamp, which will be handed over to the contractor by the purchaser.

None of the submitted documents may contain clauses that could restrict the customer in any way in the proper use of the submitted documentation or be otherwise bound to any request of the contractor for this use of documentation (see Article 17.3, paragraph (a) of the contract). Documentation with such a clause will not be approved by the CUSTOMER and will be returned to the contractor for revision.

Only SI units will be used in all documents. Drawings shall be drawn up at a scale according to applicable technical standards and rules. Drawings must be provided with a ratio scale specification. In the case of a possible scaling down of a drawing it is necessary to maintain the legibility.

Each submitted documentation in electronic and printed form will be equipped with a transmittal sheet indicating the following data (but not limited to):

date of dispatch

name of the project

data on the processor, sender and recipient

part of the project to which the documentation relates

reasons for sending

dates and description of actions to be performed by the recipient

other details assisting further processing by the recipient

list of submitted documentation or of transferred files (name, type, size, revision, etc.)

possible limitations or restrictions

## Quantity of documentation

All the above stated documentation shall be handed over to the Purchaser for approval and also in the final (approved) form in electronic form via a shared storage and in the form for approval and also in the final (approved) version in the following number of printed copies:

| Chap. | Documentation | For approval | Final version |
| --- | --- | --- | --- |
| 2.1 | Rules of administrative procedure | 3 | 3 |
| 2.2 | Time schedule of the documentation creation (PLTD) | 3 | 3 |
| 2.3 | Documentation for quality assurance | 2 | 2 |
| 2.4 | Design site facilities | 6 | 6 |
| 2.5 | Documentation for execution of the project (Design) Phase 1 – Basic design solution of the Work Phase 2 – Detailed design documentation | 6 6 | 6 6 |
| 2.6 | Documentation to application for a change in the construction before its completion (both the stages) | 3 | 10 |
| 2.7 | Principles of the construction organisation (ZOV) | 6 | 5 |
| 2.8 | OHS Plan | 6 | 5 |
| 2.9 | Accompanying technical documentation | - | 2 original copies |
| 2.10 | Design for the first commissioning | 6 | 6 |
| 2.11 | Design for the guarantee measurement | 3 | 6 |
| 2.12 | Operation regulations | 3 | 3 |
| 2.13 | Regulations for maintenance | 3 | 3 |
| 2.14 | Documents for permission of the trial operation and obtaining of the final approval to use | - | 3 |
| 2.15 | Documentation for training of the Purchaser’s staff | 2 | according to the number of the trained personnel |
| 2.16 | Documentation for execution of the Work - (incl. the List of spare parts and fast-wearing parts and the Geometric plan) | - | 1 + 10 (see Chapter 2.16) |

Based on the agreement between the purchaser and the contractor, the number of printed copies of the documentation for approval may be reduced for individual types of documentation.

At the same time, the documentation in its final form (approved) shall also always be submitted in the number of 2 pieces in a digital version on a USB/flash drive in the formats and arrangement according to the requirements stated in chapter 3.2.2.

## Documentation form

### Printed form

Printed documents and drawings shall be handed over in the formats in accordance with the ČSN standards. The format used for text documents shall be A4, the other documents shall preferably use the A4 and A3 formats.

Larger formats shall be used for the drawings which are to be subsequently folded in such a way that it can be possible to insert them into a binder of the A4 format.

If any design outputs are marked in the existing documents, their original format shall be maintained.

The original copy of each drawing sheet shall be made on a high-quality material in the form of output from the laser or ink-jet printer or plotter.

### Electronic form

#### Format of files

The drawing documentation shall be handed over in native formats of the AutoCAD program rel. 2018 (or previous - *.dwg, *.dxf). At the same time, drawings will always be submitted in *.pdf format.

Text documents shall be handed over in native formats of the MS Word 2007 program (or higher - *.doc,*.docx).

Databases, tables, lists shall be handed over in native formats of the MS Excel 2007 program (or higher - *.xls, *.xlsx).

Time and implementation schedules, detailed time and implementation schedules, actual implementation progress.

Time schedules shall be handed over in a native format of the MS Project 2021 (*.mpp). At the same time they shall always be handed over in the *.pdf format.

Graphic files (possible photograph documentation, attached as complements to the technical specification) shall be created or transformed into the *.jpg format.

Scanned documents shall be handed over in the *.pdf format.

All the electronic versions of documents shall be handed over in an “open” version (not protected by a password or other way), which will enable further processing of the file by the purchaser (editing, copying, printing, conversion to other formats, etc.).

Documentation shall be made in an editable form and without using any special superstructures (e.g. CADELEC).

Documentation that does not meet the above requirements will not be approved by the customer and will be returned to the contractor for revision.

An exception is formed only by the documents not existing at the Contractor’s place in an editable form (catalogue sheets, inspection reports, etc.).

The electronic documentation shall be accompanied by all possible non-standards fonts, libraries, line types, hatching, drawing (plotter operating) and other styles or other complements necessary for a proper and complete display of the documentation.

#### Organization of electronic documents on DIGITAL media

The documents created within the framework of the Work shall be handed over to the Purchaser in their final form (approved) on USB/flash discs.

Individual discs handed over shall be numbered by using an increasing series on the actual carrier.

Naming of electronic files and arrangement of the files on the medium must facilitate a fast, easy and unique orientation in the components and identification of the file and its content.

For this purpose, it is necessary to use a directory arrangement system with verbal description of folders, and comprehensible names of individual files shall be used.

A file shall be stored on each medium handed over (named “Obsah USB.docx” or “Obsah USB.xlsx”), indicating the directory structure used, together with the names of individual files, their storage in individual folders and a brief description of the content of the files.

For storing files on shared storage, the system, method, rules and its location for storing documentation will be agreed upon by the purchaser in advance within the Rules of administrative procedure.

## Language of the documentation

All the documentation shall be delivered in the Czech language. It is allowed to use descriptions in English on drawings, with a legend of the expressions with a translation into Czech.

An exception is admitted only for specific documentation for HW and SW of the control system or original catalogue sheets of the imported equipment delivered, which may be in a foreign language – the Purchaser in this case requires the English language.

The attestations of the equipment shall be delivered with a Czech translation.

# Coding

The Purchaser requires implementation of the equipment marking and coding system within the KKS system.

The marking and coding system selected must be applied in a uniform way in the entire documentation for all the equipment delivered and must follow the marking of existing equipment.

# Approval of the documentation

The Contractor shall prepare and in the deadlines agreed upon gradually submit the documentation drawn up for this Work to the Purchaser for approval.

The Contractor shall hand over the documentation for approval on a gradual basis, while meeting the deadlines in the time schedule provided for in the Contract and Chapter 7 below.

Each documentation handed over for approval shall be equipped with an accompanying sheet compliance with the above-mentioned rules for submitting documentation in chapter 3.

Every subsequent revision of the documentation shall include a list of changes against the previous version approved. The changes against the previous approved version shall be made in the documentation handed over for approval by way of revisions (text part, lists) or highlighted with “clouds” (drawings).

Within fifteen (15) business days after the Purchaser’s receiving any documentation for approval in a provable way, it shall either return the approved copy to the Contractor or it shall notify the Contractor in writing that the document has not been approved and shall state the reasons of the non-approval. Upon the consent of the contracting parties it is possible to approve the documentation in writing even without returning the documentation.

In the case that the documentation or its integrated part (e.g. SO, IO, PS) handed over by the Contractor for approval is incomplete and the Purchaser therefore does not have a possibility of properly checking the documentation, the Purchaser shall announce it to the Contractor without any delay and the above mentioned 15-day period shall start running again after receiving the required explanation documentation / information. The same procedure shall be applied if any documentation cannot be approved due to the fact that it includes errors, irregularities or deviations from the Contract or inaccuracies and the Contractor is asked to modify the documentation and to submit the same for a new approval.

In the case of non-approval of the documentation by the Purchaser in accordance with the Contract, the Contractor shall correct the documentation and shall hand it over again to the Purchaser for approval. The process of documentation approval shall take place according to previous paragraphs provided that the reason for non-approval can be only (i) newly corrected parts of the documentation or (ii) other, even though already approved parts of the documentation affected by this correction, which cannot fully resolve the reservations of the Purchaser, that led to the non-approval of the documentation.

The parts of the documentation to which the Purchaser did not raise any objections and which therefore were not a reason for the non-approval, shall be considered as approved by default, and the Contractor is authorised to carry out works on the basis of this part of the documentation.

The Purchaser can refuse approving for only such documentation that is in contradiction with provisions of the Contract or in contradiction with good engineering practices.

The approval by the Purchaser of the documentation, whether with modifications or without them shall not release the Contractor from any of its obligations to meet all the Contract requirements, and it does not release the Contractor from responsibility for correction of that documentation either.

The deadlines for the handover of the documentation provided for in the Contract shall apply to the approved documentation. Any possible delay in the Work caused by the fact that the Contractor has failed to achieve approval of documentation within the presupposed deadlines shall be fully to the detriment of the Contractor.

# Data to be handed over by the Purchaser

Besides the data, drawings and other documents forming the content of the Contract, the Contractor shall receive, in one copy in the Czech language, the following documentation:

Available investigations and surveys,

Available as-built documentation where the Contractor connects to the existing equipment of the Purchaser.

# Documentation handover deadlines

The documentation drawn up by the Contractor shall be handed over to the Purchaser in the following (relative) deadlines:

| Chap. | Document | Deadlines for handover to the Purchaser |
| --- | --- | --- |
| 1 | Database (list) of the documentation handed over | on an ongoing basis together with each documentation handed over (even a part or revision of the documentation) |
| 2.1 | Rules of administrative procedure | No later than 45 days after the signing of the Contract |
| 2.2 | Time schedule of the documentation creation (PLTD) | No later than 60 days after the signing of the Contract |
| 2.3 | Documentation for quality assurance: |  |
|  | Quality Plan (for the Work as a whole) | No later than 60 days after the signing of the Contract |
|  | Inspection and Test Plans drawn up for individual time phases and individual SO/IO/PS/DPS: |  |
|  | designing (construction solution) | No later than 60 days after the signing of the Contract |
|  | own production | No later than 60 days before commencement of production |
|  | building work and erection | No later than 60 days before commencement of site works |
|  | Commissioning | No later than 60 days before Commissioning commencement |
|  | trial operation | No later than 60 days before trial operation commencement |
|  | Test programmes: |  |
|  | for FAT | No later than 30 days before FAT commencement |
|  | for Commissioning | No later than 60 days before Commissioning commencement |
|  | Inspection and Test Book | complemented on an ongoing basis according to the progress of inspections and tests; the complete Inspection and Test Book shall be handed over to the Purchaser before the signing of PAC |
| 2.4 | Design for the site facilities | No later than 60 days after the signing of the Contract |
| 2.5 | documentation for execution of the project – phase 1 (Basic solution of the Work and of the progress of its implementation) | No later than 120 days after the signing of the Contract |
|  | documentation for execution of the project – phase 2 (Detailed design documentation for implementation of the Work) | No later than 30 days before commencement of appropriate works on site, or before production commencement |
| 2.6 | Documentation to application for a change in the construction before its completion: Stage 1 (documentation of changes arising in the course of preparation of the Design phase 1) Stage 2 (documentation of changes arising in the course of preparation of the Design phase 2 and in the course of Commissioning) | No later than 60 days before commencement of works on the site No later than 60 days before the signing of PAC |
| 2.7 | Principles of the construction organisation (ZOV) | No later than 30 days before site works commencement |
| 2.8 | OHS Plan | No later than 30 days before site works commencement |
| 2.9 | Accompanying technical documentation | No later than 30 days before Commissioning commencement |
| 2.10 | Design for the first commissioning | No later than 30 days before Commissioning commencement |
| 2.11 | Design for the guarantee measurement for verification of individual guaranteed parameters: |  |
|  | draft methodology | No later than 10 months after the signing of the Contract |
|  | Design guarantee measurement | No later than 4 months before complex tests commencement |
| 2.12 | Operation regulations |  |
|  | provisional | No later than 60 days before Commissioning commencement |
|  | definitive (final version) | No later than 6 months after the signing of the PAC |
| 2.13 | Regulations for maintenance | No later than 60 days before the signing of PAC |
| 2.14 | Documents for trial operation permit Documents for obtaining of the final approval to use | No later than 45 days before Commissioning commencement No later than 30 days before the end of the trial operation |
| 2.15 | Documentation for training of the Purchaser’s staff | No later than 60 days before Commissioning commencement |
| 2.16 | Documentation for execution of the Work (incl. the list of the spare parts and fast-wearing parts and the Geometric layout plan) | one (1) complete set with marked changes before the signing of PAC ten (10) complete sets of the final version within 60 days after the end of the trial operation |

All the above mentioned deadlines concern the handover of the documentation approved by the Purchaser. The above mentioned deadlines can be updated on the basis of an agreement of the Parties in the Detailed time and execution plan of implementation of the Work drawn up in accordance with paragraph 24.2 of the Contract.

The documentation handed over by the Purchaser shall be handed over in the following deadlines:

| Document | Deadlines for handover to the Contractor |
| --- | --- |
| Available As-built documentation where the Contractor connects to the existing equipment of the Purchaser | na later than 15 days after contractor’s request |