PROCUREMENT DOCUMENTS for public contract Ref.no. Z2022-047348

Waste-to-Energy Facility, EVO – Komořany, Most

part 4 FORMS AND DETAILED INSTRUCTIONS FOR REQUESTS TO PARTICIPATE AND TENDERS

CONTENTS:

Request to participate	3

Volume A Tender Cover Letter	18

Volume B Draft Contract for Work	21

Volume C Enclosures to the Draft Contract for Work	26

Volume C1 Client’s Requirements for the Technical Solution of the Work	28

Volume C2 Guaranteed Parameters	30

Volume C3 Documentation	32

Volume C4 Timetable and Execution Plan for the Work	34

Volume C5 Organization of the Work	37

Volume C6 Client’s Cooperation	39

Volume C7 Training	41

Volume C8 List of Subcontractors	43

Volume C9 Performance and Advance Payment Bank Guarantees	45

Volume C10 Price Specifications	47

Volume C11 Roadmap of Key Work Milestones and Prices	49

Volume C12 Rules for the Economic Operator	52

Volume C13 Contractor’s Technical Specifications	54

Volume C14 Information on processing of personal data obtained from the data subject and from other sources	126

# Request to participate

- Economic operators shall prepare and submit requests to participate in accordance with the Procurement Documents, particularly Articles 13 through 16 of Part 1 of the Procurement Documents.

- The request to participate must contain the Identification Sheet included below in Annex 1.

- As part of their requests to participate, economic operators shall submit documents demonstrating their qualifications according to the contracting authority’s requirements given in Article 14 of Part 1 of the Procurement Documents.

- Economic operators shall use the template Affidavit listed below in Annex 2 to demonstrate proof of basic qualification pursuant to paragraph 14.1.1.

- Pursuant to paragraph 14.1.2.d), economic operators shall also demonstrate its qualifications under paragraph 14.1.2 c) using the List of Professionally Qualified Individuals to demonstrate professional qualification included in Annex 8.

- To demonstrate qualifications pursuant to paragraph 14.1.3 a), and together with its income statement or similar document pursuant to the laws applicable to the economic operator’s registered office, the economic operator shall provide an affidavit stating the economic operator’s total turnover for the last three immediately preceding periods, or for all periods from its establishment if the economic operator was established in such three-year period. A template of the affidavit is included below in Annex 3.

- Qualifications pursuant to Article 14.1.4 a) shall be demonstrated using the template of the List of Construction Projects executed by the economic operator over the past 12 years, which is included below in Annex 4.

- A request to participate must contain the Affidavit on lack of any conflicts of interest. A template of the affidavit is included below in Annex 5.

- A request to participate must contain an Affidavit on restrictive measures relating to sanctions connected to the infringement of international rights and the conflict in Ukraine. A template of the affidavit is included below in Annex 7.

Annex 1 - Identification sheet

- IDENTIFICATION SHEET

Public Contract: 
Waste-to-Energy Facility, EVO – Komořany, Most

Contracting authority for the public contract:

United Energy, a.s., Most – Komořany, Teplárenská 2, Postcode 434 03, a company registered in Section B, File 1722 of the Commercial Register of the Regional Court of Ústí nad Labem, Company Reg. No.: 273 09 959

Request to participate submitted by the following economic operator:

| Economic operator’s trading name: |  |
| --- | --- |
| Economic operator’s registered office: |  |
| Company registration number: |  |
| Tax ID number: |  |
| a company registered | in Section ......, File ........ of the Business Registry of the [court name} |
| First and last names of all authorised signatories: |  |
| Signatories’ manner of representation and signature on behalf of the company, as listed in the Business Registry: |  |
| ID of the economic operator’s data mailbox: |  |
| Economic operator’s contact person for the contracting authority for matters involving the request to participate: |  |
| First and last name: |  |
| Address: |  |
| Telephone: | ................................... / mobile: .............................. |
| Mail: |  |

After reviewing the Notice of the Commencement of the Proceedings for a public service (“Notice”), and the Procurement Documents, we, the duly authorized and the undersigned, submit our request to participate in the negotiated procedure with prior publication as supported by the relevant documentation to demonstrate our fulfilment of the qualifications under the Notice and the Procurement Documents.

We declare that all the requirements laid down in the Notice and the Procurement Documents are clear and comprehensible to us and all data and details specified in our request to participate are based on facts and are true.

We likewise declare that we have not withheld any material facts in our request to participate that could impact fulfilment of the qualifications or assessment of our qualifications pursuant to the Procurement Documents.

We make this statement on the basis of our clear, comprehensible, deliberate and free will, and we are aware of all the consequences of providing false information.

In ………………. dated ………		………………………………………………

Full name and signature
of the economic operator’s authorised representative

Annex 2 – Template Affidavit

Affidavit

Contract: Waste-to-Energy Facility, EVO – Komořany, Most

I, the below-signed authorised representative of the economic operator,

……………………… with registered office at .............................. Company Reg. No. ........................,

hereby declare that the economic operator:

- has not been convicted of an offence in the country of its registered office in the last 5 years prior to the commencement of the procurement procedure for an offence listed in Enclosure 3 to Act No. 134/2016 Coll., on Public Procurement, or a similar offence under the law of the economic operator's country of residence; expunged convictions are not taken into account.

- If the economic operator is a legal person, this legal person and every member of its governing body have also fulfilled this condition. If a member of the economic operator's governing body is a legal person, this legal person, every member of the governing body of this legal person and person representing such legal person in the economic operator’s governing body have fulfilled this condition.

- If the Participant is a branch office of a foreign legal person, such legal person and the head of the branch office must fulfil this condition. If the Participant is a branch office of a Czech legal person, such legal person, every member of the governing body and the head of the branch office must fulfil this condition.

- has no outstanding tax arrears registered in tax records in the Czech Republic or in the country of its registered office,

- has no outstanding arrears in respect of payments and penalties of public health insurance in the Czech Republic or in the country of its registered office,

- has no outstanding arrears in respect of payments and penalties of social security contributions and contribution to the national employment policy in the Czech Republic or in the country of its registered office,

- is not in liquidation, has not been declared insolvent, in respect of whom the receivership has been imposed under another legal regulation, and the economic operator is not in a similar situation pursuant to the law of the country of the economic operator's registered office.

We make this statement on the basis of our clear, comprehensible, deliberate and free will, and we are aware of all the consequences of providing false information.

In......………..........          dated....................

Signature

[natural person - entrepreneur / governing body / all members of the governing body / member (members) of the governing body authorised to sign on behalf of the legal person / head of a branch of a foreign legal person / natural person authorised to act on behalf of a legal person].

.................................................................

Full name and signature
of the economic operator’s authorised representative

Annex 3 - Template affidavit on the economic operator’s total turnover

- Economic operator’s turnover statement

Public Contract: 
Waste-to-Energy Facility, EVO – Komořany, Most

Economic operator:

………………………………….. with registered office at ................................................ Company Registration no. .......................,

hereby declare that it has generated the following total turnover in the three most recent accounting periods:

| Accounting period | 2019 | 2020 | 2021 |
| --- | --- | --- | --- |
| Total turnover / currency |  |  |  |

In......………..........dated.....................

....................................................................

Full name and signature
of the economic operator’s authorised representative

If the accounting period is a business year, the economic operator shall provide data for the three most recent business years.

Addendum 4 - Template list of construction projects executed by the economic operator over the past 15 years

- List of construction projects executed by the economic operator over the past 15 years

Public Contract: Waste-to-Energy Facility, EVO – Komořany, Most

Economic operator:

……………………… with registered office at .............................. Company Registration no. ..................,

in compliance with the contracting authority’s request of Article 14, paragraphs 14.1.4-a of Part 1 of the Procurement Documents, hereby presents the following construction projects (contracts), duly executed and completed in the past 15 years:

| i) delivered, installed and commissioned waste-to-energy plants with a capacity of at least 90,000 t / year as the lead contractor (if several contractors were involved in a consortium, then as the lead member of such consortium) |  |  |
| --- | --- | --- |
| 1. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| n. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| ii) delivered, installed and commissioned waste-to-energy plants with a capacity of at least 90,000 t / year |  |  |
| 1. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| n. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| iii) delivered, installed, and commissioned, as a subcontractor to a lead contractor or third party within their execution for waste-to-energy plants, a grate-firing waste incineration boiler with a capacity of at least 90,000 t / year and can at the same time provide a reference for the delivery, installation, and commissioning of flue gas treatment equipment for waste-to-energy plants with a capacity of at least 90,000 t / year either itself or via subcontractors or members of a consortium |  |  |
| 1. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| n. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| iv) as contractor commissioned a waste incineration boiler for waste-to-energy plant with a capacity of at least 90,000 t / year. |  |  |
| 1. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |
| n. | Contract name: |  |
|  | Economic operator’s trading name: |  |
|  | Contract location: |  |
|  | Subject of contract: |  |
|  | Period of execution: |  |
|  | Date of project acceptance by client: |  |
|  | Client trading name: |  |
|  | Client reference (first and last name of client representative able to confirm reference, incl. phone and e-mail): |  |
|  | Brief description of project scope and basic parameters: |  |

The projects listed above meet in full the criteria of the qualification required by Paragraph 14.1.4-a of Part 1 of the Procurement Documents.

In ......……….......... on ....................

.....................................................................

Participant authorized representative full name and signature

Annex 5 - Template affidavit on lack of any conflicts of interest

- Affidavit on the lack of any conflict of interests pursuant to Section 4b of Act 159/200 Coll. on Conflicts of Interest, as amended

Public Contract: 
Waste-to-Energy Facility, EVO – Komořany, Most

Economic operator:

………………………………….. with registered office at ................................................ Company Registration no. .......................,

hereby declares:

- in matters concerning the public contract with the name “Waste-to-Energy Facility, EVO Komořany, Most” does hereby declare that it is not a commercial company in which a public official as stipulated in Section 2 (1)(c) of Act 159/2006 Coll. on Conflicts of Interest, as amended (a member of the government or the head of another central administrative office, not headed by a member of the government) or a person controlled by them holds an ownership interest of at least 25% of a partner’s share in a company;

- a subcontractor via which it demonstrates qualifications (if such exists) is not a company in which in which a public official as stipulated in Section 2 (1)(c) of Act 159/2006 Coll. on Conflicts of Interest, as amended (a member of the government or the head of another central administrative office, not headed by a member of the government) or a person controlled by them holds an ownership interest of at least 25% of a partner’s share in a company;

In......………..........dated.....................

....................................................................

Full name and signature
of the economic operator’s authorised representative

Annex 6 - Template List of professionally qualified individuals to demonstrate professional qualification

List of professionally qualified individuals to demonstrate professional qualification

Public Contract: 
Waste-to-Energy Facility, EVO – Komořany, Most

Economic operator:

………………………………….. with registered office at ................................................ Company Registration no. .......................,

hereby provide a list of professional qualified persons via which it demonstrates professional qualification and declares that such persons will perform the specified tasks within the contract:

Pursuant to Art. 14 Subs. 14.1.2 c) Part 1 of the Procurement Documents

| Authorised person in the field of civil engineering pursuant to Section 5 (3)(a) of Act 360/1992 on the profession of chartered architect and chartered civil engineer and chartered civil engineering technicians. |  |
| --- | --- |
| First and last name of the professionally qualified person | completed by the economic operator |
| Document certifying professional qualification (name) / document number / date of issue | completed by the economic operator |
| Copy of the document submitted in the tender | YES |
| Is this person employed by the economic operator | YES / NO completed by the economic operator |
| Name of the company where the person is employed (if not employed by the economic operator) | completed by the economic operator |

| Authorised person in the field of technological equipment of buildings pursuant to Section 5 (3)(e) of Act 360/1992 on the profession of chartered architect and chartered civil engineer and chartered civil engineering technicians. |  |
| --- | --- |
| First and last name of the professionally qualified person | completed by the economic operator |
| Document certifying professional qualification (name) / document number / date of issue | completed by the economic operator |
| Copy of the document submitted in the tender | YES |
| Is this person employed by the economic operator | YES / NO completed by the economic operator |
| Name of the company where the person is employed (if not employed by the economic operator) | completed by the economic operator |

The economic operator declares that it is aware of all the consequences of making false statements in this list.

In ………………. dated ………

...........................................................................

Full name and signature
of the economic operator’s authorised representative

Notes:

Instructions for completing the list of professionally qualified individuals to demonstrate professional qualification and requirements for submitting documents:

##### The economic operator shall specify if each professionally qualified person is also the economic operator’s employee.

##### If the person is employed by the economic operator, the economic operator is not required to submit any additional documents except for a copy of the relevant document certifying professional qualification in accordance with Paragraph 14.1.2 c) of Part 1 of the Procurement Documents.

If a person with professional qualification is not employed by the economic operator (a subcontractor is involved), the economic operator shall specify the name of the company where such person is employed. If this professionally qualified person is a subcontractor to the economic operator (self-employed) or an employee of a company that is the economic operator’s subcontractor, the economic operator shall identify such subcontractor in the indicative tender in the List of Subcontractors – Enclosure 8 of Part 2 of the Procurement Documents and submit the documents specified in Paragraph 14.4.1 of Part 1 of the Procurement Documents.

Annex 7 - Template Affidavit on restrictive measures relating to sanctions connected to the infringement of international rights and the conflict in Ukraine

- Affidavit on restrictive measures relating to sanctions connected to the infringement of international rights and the conflict in Ukraine

Economic operator:

| Trade name |  |
| --- | --- |
| Registered address |  |
| Company registration number |  |

hereby, in relation to the public contract entitled “Waste-to-Energy Facility, EVO Komořany, Most”, declares that

- neither it nor any of its subcontractors or other persons according to Section 83 of Act No. 134/2016 Coll. on public procurement, as amended, who shall participate in the performance of this public contract to an extent of more than 10 % of the tendered price,

- is a Russian national, a natural person or a legal person or an entity or a body having its registered office in Russia,

- is not more than 50% owned, directly or indirectly, by any of the subjects specified in a), and

- is not acting on behalf of or at the instruction of any of the subjects specified in a) or b).

- is not a person specified in the sanctions list in the annex to Council Regulation (EU) No 269/2014 of 17 March 2014 concerning restrictive measures in respect of actions undermining or threatening the territorial integrity, sovereignty and independence of Ukraine *as amended by subsequent addenda) or Council Regulation (EC) No 765/2006 of 18 May 2006 concerning restrictive measures against President Lukashenko and certain officials of Belarus (as amended by subsequent addenda).

- it shall not, either directly or indirectly, make available any financial means which it receives for performance of the public contract to natural persons or legal persons, entities, or bodies associated with them, or to the benefit thereof, stated in the sanctions list in the annex to Council Regulation (EU) No 269/2014 of 17 March 2014 concerning restrictive measures in respect of actions undermining or threatening the territorial integrity, sovereignty and independence of Ukraine *as amended by subsequent addenda) or Council Regulation (EC) No 765/2006 of 18 May 2006 concerning restrictive measures against President Lukashenko and certain officials of Belarus (as amended by subsequent addenda).

In ………………. dated ………

....................................................................

Full name and signature
of the economic operator’s authorised representative

# Volume A Tender Cover Letter

- In this Volume A of the indicative tender / tender, the participant shall submit a Tender Cover Letter completed per the cover letter template given below and signed as required by Paragraph 21.5 or 27.3 of Part 1 of the Procurement Documents. If the signatory is authorised by the participant’s statutory representative, the relevant power of attorney or letter or authorisation must be submitted within this Volume A.

Cover letter template:

Economic operator / participant:

| Economic operator / participant’s trading name: |  |
| --- | --- |
| Economic operator / participant’s registered address: |  |
| Company registration number: |  |
| Tax ID number: |  |
| a company registered | in Section ......, File ........ of the Business Registry of the [court name] |
| First and last names of all authorised signatories: |  |
| Signatories’ manner of representation and signature on behalf of the company, as listed in the Business Registry: |  |
| Data Box ID |  |

To: 	United Energy, a.s.
Most – Komořany, Teplárenská 2, Postcode 434 03, Czech Republic

Date: 	.....................................

Re:	Indicative tender / Tender for the public contract
“Waste-to-Energy Facility, EVO Komořany, Most“
Ref. no. ...................

To whom it may concern,
Based on your invitation to submit indicative tenders / tenders dated ................... we, the duly authorized and the undersigned, hereby offer to execute to the public contract named “Waste-to-Energy Facility, EVO Komořany, Most” in the scope and under the conditions laid down in your Procurement Documents.

The total tendered price for execution of the work (excluding VAT valid in the Czech Republic) per our submitted indicative tender / tender ref. no. ........................., totals CZK ..................... CZK and EUR ....................

We hereby declare that, before submitting our indicative tender / tender, we have obtained and familiarized ourselves with all information required to clearly specify the quantities and types of goods, works, and services that are to be delivered in the execution of this public contract, as well as with your terms as given in the Procurement Documents, and that these are clear and understood by us.

Our representative authorized to negotiate with you, the contracting authority, in matters of our indicative tender / tender, shall be:

| First and last name: |  |
| --- | --- |
| Address: |  |
| Telephone: | ................................... / mobile: .............................. |
| Fax: |  |
| Mail: |  |

.........................................................................................

(Signature of the authorised representative of the economic operator / participant)

Note: text highlighted in turquoise will be adapted by the economic operator depending on the phase of the procurement process

- Volume A of the tender shall also include the security pursuant to Article 28 of Part 1 of the Procurement Documents.

# Volume B Draft Contract for Work

- In Volume B of the indicative tender / tender the participant shall submit the draft contract for work (i.e., the text of the draft contract for work itself, without enclosures) as prepared by the contracting authority and is contained in the introduction to Part 2 of the Procurement Documents.

- Within preparation of its indicative tender / tender, the participant shall enter the details required by the contracting authority in Article / Paragraph 1.7.1 (e) and 13.1 into the draft contract for work (the text of the draft contract for work excluding any enclosures).

The participant shall also enter the offered warranty period into Paragraph 45.1.1.1 of the draft contract for work within the preparation of its indicative tender / tender for the following

- Grate

- Protection for heat transfer surfaces

- Outlet superheater

The warranty period must be offered for a minimum of 24 months, whereby any offered extension(s) must be in full multiples of 12 months.

- The draft contract for work submitted within the tender must then be signed in accordance with the provisions of Paragraph 27.3  of Part 1 of the Procurement Documents.

- Participants may, as part of their indicative tenders, propose minor adjustments to the draft contract text, insofar as such may improve clarity and/or transparency (remove ambiguities or errors), and provided that no such adjustment materially impacts the client / contracting authority’s rights or the economic operator / contractor's obligations.

- The Participant’s potential adjustments as described in the preceding paragraph shall also be submitted in this Volume B of the indicative tender as a separate document based on the template given in Annex 1 to this Volume B.

- Any adjustments the participant may make to the draft contract text shall be interpreted as comments by the contracting authority. On the basis of such comments, the contracting authority may decide to change the Procurement Documents during the indicative tender negotiations phase pursuant to Article 25 of Part 1 of the Procurement Documents. That is, Participants will not be able to stipulate their own changes and amendments to the Contract. In no event shall the contracting authority be bound to accept partial changes proposed pursuant to Point 3 above.

- If the participant has no adjustments to the draft contract to propose, this Volume B shall, in addition to the draft contract, contain the participant’s statement to the effect that the participant accepts without reservation the text of the draft contract for work in the form drafted by the contracting authority and presented as the introduction to Part 2 of the Procurement Documents.

- The contracting authority reserves the right to change the text of the draft contract by amending the Procurement Documents during indicative tender negotiations pursuant to Article 25 of Part 1 of the Procurement Documents; this includes unilateral changes, if such are deemed necessary on the basis of tender negotiations.

Addendum 1
Template for Draft Contract for Work adjustment proposals

| Participant: ..................................... |  |
| --- | --- |
| Article | Name |
|  | PARTIES TO THE CONTRACT |
|  | TERMS AND DEFINITIONS |
|  | LEGAL BASIS OF THE CONTRACT |
|  | CONTRACT DOCUMENTS |
|  | APPLICABLE LAW |
|  | RESOLUTION OF DISPUTES |
|  | NOTICES |
| (Example) | Original text: |
| 7.1 (a) | Notices sent by registered mail or courier shall be considered sent, for registered mail, on the date of the receipt provided by the post office of posting (or on the day the shipment was accepted by a courier, as documented by the courier’s receipt), and shall be considered delivered on the third (3rd) day after the date marked on the post office’s receipt (date shipment was accepted by courier from sender). |
|  | Proposed change: |
| 7.1 (a) | notices sent by registered mail or courier shall be considered sent via registered main on the date on confirmation from the post office (or the date on which the shipment was accepted by a courier, as documented by the courier’s receipt) and delivered on the third second (3rd 2nd) day after the date on confirmation from the post office (or the date on which the shipment was accepted by the courier from the sender); |
|  | PURPOSE OF THE WORK |
|  | SUBJECT OF THE CONTRACT – THE WORK |
|  | WORK TIMETABLE |
|  | CONTRACTOR’S OBLIGATIONS IN EXECUTION OF THE WORK |
|  | CLIENT’S COOPERATION |
|  | CONTRACT PRICE |
|  | TERMS OF PAYMENT |
|  | TAXES, CUSTOMS AND FEES |
|  | BANK GUARANTEES FOR THE WORK AND FOR THE DEPOSIT |
|  | LICENSES AND RIGHTS OF USE TO TECHNICAL INFORMATION |
|  | CONFIDENTIALITY REGARDING INFORMATION AND CONTRACTUAL DOCUMENTS ETHICAL CONDUCT BETWEEN THE PARTIES |
|  | PARTIES‘ REPRESENTATIVES |
|  | INFORMATION SUBMITTED TO CLIENT |
|  | SUBCONTRACTING |
|  | STANDARDS AND LEGISLATION |
|  | ENGINEERING WORK, DOCUMENTATION |
|  | EXECUTION OF THE WORK |
|  | DELIVERY AND DOCUMENTATION |
|  | PACKAGING INSTRUCTIONS |
|  | TRANSPORT |
|  | WORK QUALITY ASSURANCE |
|  | ASSEMBLY AND MECHANICAL COMPLETION |
|  | COMMISSIONING |
|  | PROVISIONAL ACCEPTANCE OF THE WORK |
|  | TRIAL OPERATION |
|  | GUARANTEE MEASUREMENT DURING TEST “B“, FINAL ACCEPTANCE OF THE WORK |
|  | FULFILMENT OF THE CONTRACTOR’S OBLIGATIONS |
|  | EMERGENCY WORKS |
|  | TRAINING FOR THE CLIENT’S OPERATIONS AND MAINTENANCE STAFF |
|  | REPLACEMENT PARTS AND RAPID-WEAR PARTS |
|  | POST-WARRANTY SERVICING |
|  | SITE AND ASSEMBLY SITES |
|  | ADMINISTRATION RULES, OCCUPATIONAL HEALTH AND SAFETY |
|  | WASTE MANAGEMENT, ENVIRONMENTAL PROTECTION |
|  | WORK SECURITY |
|  | GUARANTEED PARAMETERS |
|  | CONTRACTUAL PENALTIES |
|  | LIABILITY FOR DEFECTS, QUALITY GUARANTEE |
|  | COMPENSATION FOR DAMAGE, LIMITATION OF LIABILITY |
|  | REIMBURSEMENT FOR PATENT CLAIMS |
|  | TRANSFER OF OWNERSHIP |
|  | DUE CARE OF THE WORK, TRANSFER OF LIABILITY FOR DAMAGE TO THE WORK |
|  | PROPERTY LOSS AND DAMAGE, PERSONNEL ACCIDENT AND INJURY, CLAIM SETTLEMENT |
|  | INSURANCE |
|  | FORCE MAJEURE |
|  | CHANGE PROCEEDINGS |
|  | INTERRUPTION OF WORKS |
|  | WITHDRAWAL FROM THE CONTRACT |
|  | ETHICAL CONDUCT BETWEEN THE PARTIES |
|  | FINAL PROVISIONS |

# Volume C Enclosures to the Draft Contract for Work

This Volume C - Enclosures to the Draft Contract for Work shall be for the purposes of the indicative tenders / tenders further divided into Volumes C1 to C14 as specified below.

# Volume C1 Client’s Requirements for the Technical Solution of the Work

- In this Volume C1 of the indicative tender / tender the participant shall submit Enclosure 1 – Client’s Requirements for the Technical Solution of the work, prepared by the contracting authority and contained in Part 2 of the Procurement Documents in connection to Part 3 of the Procurement Documents.

- The participant is not authorised to make any changes to Enclosure 1.

- No annexes to Enclosure shall be submitted with indicative tender / tender.

Note:

Following on from paragraph 5 and 6 of the instructions for compiling Volume 13 (Enclosure 13 - Contractor’s technical specifications) found hereunder in this Part 4 of the Procurement Documents, the contracting authority is ready to consider proposed departures which facilitate a solution for waste-to-energy facilities other than presented in the technical conditions presented in Enclosure 1 - Client’s Requirements for the Technical Solution of the Work, if it is duly shown that it is a solution which is fully equivalent or better from all technical, qualitative, capacity, lifetime, reliability, environmental, and other perspectives.

# Volume C2 Guaranteed Parameters

- In this Volume C2 of the indicative tender / tender the participant shall submit Enclosure 2 - Guaranteed Parameters, prepared by the contracting authority and contained in Part 2 of the Procurement Documents and in accordance with the instructions provided below.

- In the preparation of the indicative tender / tender, the participant shall only enter the data required by the contracting authority and specified in the chapters of Enclosure 2 within Enclosure 2:

- Chapter 2.3, values marked with “entered by the participant”, i.e. in the table

  - “The type and concentration the reducing agent to reduce oxides of nitrogen”,

  - the value under point 2.3.1 in the “Guarantee parameters” table,

  - the values under points 2.3.2 to 2.3.8 in the "Specific consumption of reagents for capturing acid components of flue gases and heavy metals” table,

  - the values under points 2.3.9.1 to 2.3.9.n in the "Other reagents for the capture of acid components of flue gases and heavy metals:” table,

  - the values under points 2.3.10 to 2.3.14 in the “Specific consumption of reagents for wastewater treatment and chemical feed water treatment” table

  - the values under points 2.3.15.1 to 2.3.15.n in the “Other reagents for wastewater treatment and chemical feed water treatment”, and

  - data in the “demonstration (testing) conditions” table.

- the values marked with “entered by the participant” under points 2.5.1 to 2.5.7 in Chapter 2.5,

- the values marked with “entered by the participant” under points 2.6.3 to 2.6.5 in Chapter 2.6,

- the value marked with “entered by the participant” under point 2.7.1 in Chapter 2.7,

- the values marked with “entered by the participant” under points 2.8.1 to 2.8.6 in Chapter 2.8,

- the values marked with “entered by the participant” under points 2.10.1 to 2.10.7 in Chapter 2.10,

- the value marked with “entered by the participant” under point 2.11.1, 2.11.2, and 2.11.3 in Chapter 2.11,

- the value marked with “entered by the participant” under point 2.12.1 in Chapter 2.12.

# Volume C3 Documentation

- In this Volume C3 of the indicative tender / tender the participant shall submit Enclosure 3 - Documentation, prepared by the contracting authority and contained in Part 2 of the Procurement Documents and in accordance with the instructions provided below.

- The participant is not authorised to make any changes to Enclosure 3.

# Volume C4 Timetable and Execution Plan for the Work

- In this Volume C4 of the indicative tender / tender the participant shall submit Enclosure 4 – Timetable and Execution Plan for the Work. The participant shall prepare this Enclosure and incorporate all the contracting authority’s requirements in it.

  - The Timetable and Execution Plan for the work shall describe all activities of the economic operator / participant / contractor and any subcontractors it may engage in the execution of the work

  - The Timetable and Execution Plan for the Work shall include the period from signature of the Contract for Work to signature of the certificate of provisional acceptance of the work, including the subsequent trial operation of the work, and at the same time it shall respect all milestones specified by the Contracting Entity in provisions of paragraph 10.1 of the Draft Contract for Work, Part 2 of the Procurement Documents and at the same time the deadlines for the handover of the documentation provided for in Chapter 7 of Enclosure 3 of the contract.

  - The Timetable and Execution Plan for the work shall contain time evaluation in particular of the below stated activities:

    - Conclusion of the contract for work (the starting point for the Timetable and Execution Plan) with the expected date of contract signature 21. 12. 2023.

    - Deadlines of fulfilment of individual milestones of partial payments of the contract price in accordance with the enclosure 11 of the contract.

    - Handover of the administrative order for the work prepared by the contractor and approved by the client, in accordance with Enclosure 3 of Part 2 of the Procurement Documents.

    - Handing over of the Documentation Preparation Plan (PLTD) prepared by the contractor and approved by the client, in accordance with Enclosure 3 of Part 2 of the Procurement Documents.

    - Handover of the individual phases of the Documentation for Execution of the Project prepared by the contractor and approved by the client, in accordance with Enclosure 3 of Part 2 of the Procurement Documents.

    - Handover of other documentation for the work prepared by the contractor and approved by the client, in accordance with Enclosure 3 of Part 2 of the Procurement Documents.

    - Handing over of the site of the work.

    - Procurement of material, manufacture and supplies.

    - Plan of construction and completion of individual building structures (SO).

    - Progress of assembly on individual process systems (PS) and partial process systems (DPS)

    - Mechanical completion of individual process systems / partial process systems (PS / DPS), incl. execution of individual tests of individual process systems / partial process systems (PS / DPS).

    - Mechanical completion of the work.

    - Training of the Client's personnel within the framework of the work.

    - Commencement and completion of complex tests of the work, including test “A”.

    - Commencement and completion of performance test of the work.

    - Provisional acceptance of the work . 
The participant shall specify the earliest realistic date of provisional acceptance of the work, a maximum of thirty six (36) months from the expected date of signature of the contract for work in accordance with the Contract Notice – Public Services, ref. no.................... and the Procurement Documents.

    - Trial operation of the work.

  - Besides the time data stated therein, the time schedule shall inform about content of individual steps of execution of the work and at the same time provide further information for coordination of the work and simultaneously implemented projects and activities of the Client.

  - The Time and Implementing Schedule of the work must prove that the work is feasible in the deadlines required by the Contracting Entity in Part 2 of the Procurement Documents.

  - The Timetable and Execution Plan for the work must in particular respect all procedures stated in the Procurement Documents, such as procedures in consultation and approval of the documentation by the client etc., and initial and limiting conditions of execution of the work as stated in the Procurement Documents.

  - The Timetable and Execution Plan for the work must express in particular main relations of the design preparation, quality assurance, manufacture, supply of equipment to the site, installation and erection work, tests and inspections for the whole period of execution of the work, training, commissioning and handing over of documentation in accordance with paragraph 10.1 of the Draft Contract for Work and Enclosure 3 of Part 2 of the Procurement Documents.

  - Individual activities must be unambiguously defined from the viewpoint of their content, time evaluation, commencement and completion, and must contain logical links to subsequent activities.

  - The Timetable and Execution Plan for the work shall also include time requirements for the contracting authority’s cooperation pursuant to the provisions of Article 12 (Contracting authority’s obligations) of the Draft Contract for Work, Part 2 of the Procurement Documents and with Enclosure 6, Part 2 of the Procurement Documents.

  - The Timetable and Execution Plan for the work shall be prepared with the use of the time unit specified as a “day”.

# Volume C5 Organization of the Work

- In this Volume C5 of the indicative tender / tender, the participant shall submit Enclosure 5 - Organization of the Work. The participant shall prepare this Enclosure and incorporate all the contracting authority’s requirements in it.

- Enclosure 5 shall be prepared in accordance with the Procurement Documents and in its preparation the participant must respect and include in it in particular the below stated requirements of the contracting authority:

  - In this Enclosure, the participant shall submit the organisation chart prepared specifically for this work.

  - The organization chart submitted by the participant must clearly show in particular management, administrative activity, engineering, procurement, quality management, inspection, supervision of installation, commissioning, and links to individual subcontractors etc.

  - The chart must indicate whether a post is a working post on or outside the site and whether a function is to be performed by the contractor or subcontractor.

  - The chart must be in compliance with and show clear relations to the other parts of the indicative tender / tender, such as with the list of subcontractors stated in Enclosure 8 of Part 2 of the Procurement Documents.

  - The organization chart must also show the post of the OHS Coordinator in accordance with Act 309/2006 Coll., as amended, as provided by the contracting authority within execution of the work.

# Volume C6 Client’s Cooperation

- In this Volume C6 of the indicative tender / tender the participant shall submit Enclosure 6 - Client’s Cooperation prepared by the contracting authority and contained in Part 2 of the Procurement Documents.

- The participant shall, when preparing its indicative tender / tender, fill in the fields labelled “Required by Contractor” to list its requirements for the contracting authority’s cooperation pursuant to Paragraph 12.8 of Article 12 of the draft contract for work in Part 2 of the Procurement Documents.

# Volume C7 Training

- In this Volume C7 of the indicative tender / tender the participant shall submit Enclosure 7 – Training prepared by the contracting authority and contained in Part 2 of the Procurement Documents.

- The economic operator / participant may not make any changes to Annex 7.

# Volume C8 List of Subcontractors

- In this Volume C8 of the indicative tender / tender the participant shall submit Enclosure 8 - List of Subcontractors. The participant shall prepare this Enclosure and incorporate all the contracting authority’s requirements in it.

- The participant shall provide a list of the subcontractors who shall take part in executing the work, using the following tables, all fields of which are to be filled:

List of Subcontractors for Goods deliveries related to the Work

| Pos. | Subcontractor trading name, registered address, and Company Registration number | Subject matter of the delivery of the goods | Expected volume of subcontracting costs as a % of the total contract price. |
| --- | --- | --- | --- |
| 1. |  |  |  |
| 2. |  |  |  |
| n. |  |  |  |

List of Subcontractors for Works and Services deliveries related to the Work

| Pos. | Subcontractor trading name, registered address, and Company Registration number | Subject matter of the delivery of the works or services | Expected volume of subcontracting costs as a % of the total contract price. |
| --- | --- | --- | --- |
| 1. |  |  |  |
| 2. |  |  |  |
| n. |  |  |  |

- The contracting authority recommends that no more than 5 subcontractors are proposed by the participant for individual deliveries of goods, works, and services related to the work.

# Volume C9 Performance and Advance Payment Bank Guarantees

- In this Volume C9 of the indicative tender / tender the participant shall submit Enclosure 9 - Performance and Advance Payment Bank Guarantees prepared by the contracting authority and contained in Part 2 of the Procurement Documents and in accordance with the following instructions.

- The participant may in the process of preparing the indicative tender propose changes to this Enclosure 9 to comply with bank requirements provided that no such modifications restrict the contracting authority’s rights or the participant's / contractor’s obligations. The modifications proposed by the participant shall be made in form of revisions (the revisions shall be shown in colour without showing changes in text formatting) and / or shall be otherwise suitably highlighted / differentiated in the existing text to enable their easy identification.

- Instead of change proposals pursuant to Points 2 above, participants may include the proposed bank’s preferred forms directly in this Enclosure 9 and specifying the contracting authority's rights and the economic operator /participant’s obligations, provided these conform with the bank guarantee templates provided in Enclosure 9 of the Procurement Documents.

- Any form proposals from the proposed bank or adjustments the Participant may make to Enclosure 9 shall be discussed during the indicative tender negotiations phase pursuant to Article 25 of Part 1 of the Procurement Documents. Under no circumstances will the contracting authority be bound to accept changes or proposed forms from the expected bank.

# Volume C10 Price Specifications

- In this Volume C10 of the indicative tender / tender the participant shall submit Enclosure 10 - Price Specifications, prepared by the contracting authority and contained in Part 2 of the Procurement Documents and in accordance with the instructions provided below.

- In preparing the indicative tender / tender, the participant shall complete the price specifications using the defined table 1, which is provided in Enclosure 10 of Part 2 of the Procurement Documents.

- The participant shall complete the price specifications (table 1) in all the defined columns, i.e. it shall provide the following in the price specifications:

- the prices in CZK without VAT and EUR without VAT for individual items in the prescribed arrangement provided that the prices in CZK without VAT and EUR without VAT for individual items correspond to the subject matter of fulfilment of individual items. The participant shall also provide price of individual items also all side costs connected with implementation of the subject matter of the work according to the contract, such as transport of the goods to the site, site facilities, trial operation, etc., at the ratio of the amount of prices of individual items.

- total contract price of the work in CZK without VAT and EUR without VAT.

# Volume C11 Roadmap of Key Work Milestones and Prices

- In this Volume C11 of the indicative tender / tender the participant shall submit Enclosure 11 – Roadmap of Key Work Milestones and Prices prepared by the contracting authority and contained in Part 2 of the Procurement Documents.

- In preparing the indicative tender / tender, the participant shall complete this roadmap in the form of tables 1 and 2 contained in Enclosure 11 of Part 2 of the Procurement Documents and per the contracting authority’s requirements specified below.

  - The participant shall prepare the payment schedule (for advance payments) in the form of the provided table 1. In the table, the participant shall fill in only the amount of the advance payment equal to a maximum of 15% of the contract price for the work, in CZK without VAT and EUR without VAT, in accordance with Article 13.1 of the draft contract included in Part 2 of the Procurement Documents.

  - The participant shall specify its schedule (of partial payments towards the contract price) in the form of the provided table 2. The participant shall complete all the required columns in the schedule of payments, specifically:

      - the participant shall fill in individual 100% amounts for prices in CZK without VAT and EUR without VAT for partial fulfilment of the corresponding milestone while observing the payment amounts:

      - for the 1st part payment at an amount of 0.3% of the contract price of the work,

      - for the 2nd part payment at an amount of 1% of the contract price of the work,

      - for the 3rd part payment at an amount of 2% of the contract price of the work

      - for the 10th (next-to-last) part payment at an amount of 15% of the contract price of the work,

      - for the 11th (last) part payment at an amount of 10% of the contract price of the work.

  - The contracting authority presupposes carrying out of the payment of the contract price of the work within the framework of milestones I to XI. In the preparation of its indicative tender / tender, the participant may expand the number of milestones per the participant’s expected progress in executing the work in unconditional compliance with the conditions specified in Paragraph b) and in compliance with the conditions specified in Paragraph d) below.

  - The participant shall propose the amounts of the 4th to 9th partial payments per Enclosure 11 Roadmap of Key Work Milestones and Prices and any differentiation in the number of payments / milestones in accordance with Paragraph c) above in accordance with the material scope of such payments / milestones, whereby the participant must conform to the specified amounts of contract price payments if payment of the contract price based on progress on the work within the 4th to 6th partial payments per Enclosure 11 Roadmap of Key Work Milestones and Prices.

      - 4th partial payment (MILESTONE IV) - Order of the boiler and grate (DPS 01.03) - max. 40% of the contract price for DPS 01.03 specified by the participant in Enclosure 10 of the contract,

      - 5th partial payment (MILESTONE V) - Order of flue gas treatment (DPS 01.03) - max. 40% of the contract price for DPS 01.04 specified by the participant in Enclosure 10 of the contract,

      - 6thth partial payment (MILESTONE VI) - Order of the turbo generator set (PS 01.03) - max. 40% of the contract price for PS 02 specified by the participant in Enclosure 10 of the contract.

  - The amounts for the 4th to 9th partial payments pursuant to Enclosure 11 Roadmap of Key Work Milestones and Prices and any expansion in the number of payments / milestones pursuant to Paragraph c) above proposed by the participant shall be discussed during indicative tender negotiations under Article 25 of Part 1 of the Procurement Documents.

  - The participant must likewise comply with the condition that the time interval of at least 2 months must be observed between individual milestones, in exceptional cases it is possible to reduce the time interval to 1 month.

# Volume C12 Rules for the Economic Operator

- In this Volume C12 of the indicative tender / tender the participant shall submit Enclosure 12 – Rules for Contractors prepared by the contracting authority and contained in Part 2 of the Procurement Documents.

- The economic operator /participant shall submit a statement in Volume C12 affirming acceptance of the Rules for Contractors without reservation.

# Volume C13 Contractor’s Technical Specifications

- In this Volume C13 of the indicative tender / tender, the participant shall submit Enclosure 13 - Contractor's Technical Specifications. The participant shall prepare this Enclosure and incorporate all the contracting authority’s requirements in it.

- Enclosure 13 will be prepared in accordance with the requirements and conditions specified in the Procurement Documents

- The participant must comply with the contracting authority’s requirements in the preparation of Enclosure 13:

  - Enclosure 13 – Contractor’s Technical Specifications must allow detailed understanding of the system’s functions and an objective assessment of the technological quality of the indicative tender / tender, as well as an assessment of the degree to which the requirements specified in Enclosure 1 – Client’s Requirements for the Technical Solution of the Work have been met.

  - Technical Specification of the contractor shall be prepared for the entire scope of the work and shall contain detailed specifications of all supplies of goods, works and services including quantity of individual components in all disciplines.

- In terms of the technological and functional design and construction, provided that the technical requirements on the work given in Part 3 of the Procurement Documents – Technical Specifications are met, the economic operator /participant shall have complete freedom to apply its best knowledge and engineering experience so as to offer to the contracting authority the best available techniques (BAT). Where, in Part 3 of the Procurement Documents (Enclosure 1 – Client’s Requirements for the Technical Solution of the Work), the contracting authority specifies a preference for a particular method of execution or type of equipment, the economic operator / participant may use a different solution or method that is equivalent in terms of quality and technology. The economic operator / participant should, as part of Enclosure 13, provide its reasons for departing from contracting authority preferences; the contracting authority, however, shall not be required to accept them.

- If the economic operator / participant’s proposal as given in the indicative tender differs from the contracting authority’s technical requirements as given in Part 3 of the Procurement Documents – Technical Specifications (Enclosure 1 – Client’s Requirements for the Technical Solution of the Work), or elsewhere in the Procurement Documents, the economic operator / participant shall submit the List of Departures from Requirements in the Procurement Documents at the end of this Volume C13.

- Any proposed deviations in the work from requirements in the Procurement Documents made by the participant shall simply be interpreted as comments for the contracting authority. On the basis of such comments, the contracting authority may decide to change the Procurement Documents during the indicative tender negotiations phase pursuant to Article 25 of Part 1 of the Procurement Documents. Participants may not stipulated individual changes to any part of the contract. In no event shall the contracting authority be bound to accept partial changes proposed pursuant to Point 5 above.

The contracting authority hereby states that it is prepared to consider proposed departures pursuant to points 4 or 5 facilitating a different flue gas treatment design other than specified in the technical specifications if the participant thoroughly demonstrates that the proposed solution is fully equivalent or better in terms of all technical, qualitative, performance, service life, reliability, environmental and other aspects.

- If necessary, the economic operator / participant shall submit at the end of this Volume C13 of its indicative tender a list of all comments related to the contracting authority’s requirements for incorporation into Enclosure 13 as stipulated below.

- If there are no comments are provided in Enclosure 13, the economic operator / participant is not considered to have any comments.

- Contracting authority’s requirements when designing the facility

The participant must respect the following principles when designing the work:

When designing the heat transfer surfaces, to consider a pollution factor:

1st pass: 30%,

2nd pass: 35%,

3rd pass: 40%,

evaporator: 45%,

superheater: 50%,

economizer: 40%.

Protection from corrosion with alloy NiCr22Mo9Nb in the extent of the combustion chamber and the 1st pass, the roof of the 1st and 2nd pass, the upper part of the 2nd pass, the 1st bundle of the convection heat transfer surface (downstream of the flue gases), manholes, jets, bends. Protection with weld-on will be carried out by automatic machine, a minimum of two layers of weld-ons.

Minimum requirements for the quality of materials used for:

Membrane walls	16Mo3

Membrane wall headers	16Mo3

Evaporator in horizontal convection pass	16Mo3

Superheater	16Mo3

Economizer	P235GH

The walls of the incineration chamber at grate level will be cooled with water.

The minimum flue gas dwelling time in the boiler will be 13.5 seconds (empty passes - upstream of the first superheater bundle). This condition stands for design point D in the firing diagram in a boiler which is fouled as standard, i.e. after 4,000 hours of operation.

Maximum speed of the flue gases:

Superheaters: speed <3.8 m/s (clean pipes),

Economizer: speed <5 m/s (clean pipes).

When the boiler is operating at above 70% capacity, spraying in continual operation.

Bundles of heat transfer surfaces - the design will take account of simpler replacement, maintenance, and repair.

The first heat transfer convection surface downstream of the flue gases will be carried out as a co-flow, meaning that the steam enters on the hot side of the flue gases.

The expected, planned operating regime will have only one shut-down for cleaning a year.

NOx flue gas cleaning technology:

SCR - shall be designed to the future stricter limits of 40 mg/Nm3

Second line - The facility shall be designed such that it is possible to build a second line - to the east

The work shall be designed for incinerating waste with the following parameters:

|  |  | Unit | Average value | Range |
| --- | --- | --- | --- | --- |

| Properties of waste for input to bunker/shredder |  |  |  |
| --- | --- | --- | --- |
| Length of side (L, B, H) |  | mm | < 3000 |
| Total of three dimensions (L x B x H) |  | mm | < 5000 |
| Large pieces that pass through the shredder |  | % weight | < 25 |
| Straps |  | mm | < 2000 |

| Ferrous metals |  | % weight | < 2 | < 4 |
| --- | --- | --- | --- | --- |
| Non-ferrous metals, including aluminium (foil, composite foil, etc.) |  | % weight | < 0.8 | < 1.5 |
| Bulk density |  | kg/m3 |  | 100 - 550 |
| Ash and inert material content in original state | Ar | % weight | 28 | 10 - 40 |
| Content of all water in original state | Wr | % weight | 28 | 15 - 40 |
| Composition |  |  |  |  |
| S content in original state | Sr | % weight | 0.4 | < 0.9 |
| Cl content in original state | Clr | % weight | 0.5 | < 1.3 |
| F content in original state | Fr | % weight | 0.01 | < 0.1 |

- Enclosure 13 - Contractor’s Technical Specifications shall be prepared in the following structure and shall contain in particular:

Concept of the solution of the work and its general parameters

introduction and identification data,

basic parameters of the work as a whole (possibly with references to questionnaires)

concepts of solution of the work, including descriptions, drawings, computations and other information relating to the work as a whole from which especially the following aspects shall be clear

basic layout solution of the work, including the master plan of the construction,

dimensions and heights of building structures

applied building and technical solution of the main building structures

overall solution of the technological part of the work – descriptions of individual processes and applied technical solutions for their implementation, suppliers of individual technological nodes, technological charts of main technological processes, balance charts for basic operation modes, diagram indicating the set of admissible capacity states of the incineration plant (Firing capacity diagram) with a description of loading points, etc.

the method of additional modificationof the SCR catalyst in order to achieve a future lower NOx limit , if the CONTRACTING AUTHORITY decides to add this addition in the future - description of the method of modification, overall technological scheme with the added catalyst, connection points to the WORK, dispositional location, etc.

method of additional integration of flue gas condensation equipment (absorption heat pump) into the proposed technological chain of the WORK, if the CONTRACTING AUTHORITY decides to add this addition in the future - description of the method of integration, overall technological scheme with added equipment for flue gas condensation, connection points to the WORK, dispositional location, etc.

overall solution of the instrumentation and control system (“I&C”) – manufacturer and type of DCS (possible in an alternative way as well), distribution of functions between DCS and autonomous means supplied within the framework of the technological supply, overall configuration of the EVO control system

method of ensuring metrological order

overall solution of the electrical part (main data concerning power output and actual consumption, single-pole chart of the EVO)

method of connection of the work to the follow-up equipment and networks, limits of deliveries

what measures are applied in the design of the work for achievement of the required values of availability of the work – reliability of key elements of the technology (necessary for maintaining the operation at the EVO Plant), scope and manner of their backup features, diagnostic tools for evaluation of the necessity of preventive maintenance, etc.

what measures are applied in the design of the work for assurance of a trouble-free winter operation of the work, especially for the assurance of a possibility of a trouble-free start-up of the work from a cold state, even after a long outage and including the information whether there are any temperature limitations for this case or not.

what measures are applied in the design of the work to achieve required values of lifetime of the work and its components

level of the process automation, including the list of handling operations while starting up, shutting down and during a normal operation of the EVO Plant, which cannot be performed through the control system from the central control room and which will require an operator intervention in site.

minimum number of staff members for assurance of the EVO Plant operation in one shift (without the maintenance staff), in all operation states of the EVO Plant, including the cold start-up.

Scope of delivery

Specification of (material) supplies of goods included in the price of the work in arrangement according to building structures (SO) and process systems (PS) or partial process systems (DPS) where relevant, including specification of the manufacturer and type (possible in an alternative manner as well)

- including:

Specification of delivered special tools and special instrumentation

Specification of all lifting mechanisms

List of delivered laboratory instruments

Specification of all works (services) included in the price of the work.

Specification of all rights of use included in the price of the work

- Note:

The breakdown of supplies into individual PS assumed in Chapter 2 of Part 3 of the Procurement Documents (Technical Specifications – Enclosure 1), can be modified by the contractor in its specification of supplies and related services (in subsequently in the price specification) in reasonable cases. In particular, this concerns the cases when certain technical means of the I&C and electrical system, such as autonomous PLCs for process control, local power supply switchboards,  etc., are standard equipment of packed units or other delivered technological equipment.

Building structures

Descriptions, drawings and computations and other materials, in arrangement into individual SO (building structures) and IO (utility systems), documenting the building and technical solution of building facilities, including

information about the design of the following items

- bearing structures,

- cladding of the walls – type, fire resistance, heat resistance, noise parameters

- roof cladding – type, fire resistance, heat resistance, noise parameters

- windows – surface finish, shade, kind, type, material, control, heat-transfer coefficient, noise parameters

- doors, gates – kind, type, material, control, heat-transfer coefficient, fire resistance, surface finish, noise parameters

- floors,

- soffits,

- surface finishing,

- coating (specification of coating systems and used colour shades),

- final treatment,

- structures for lifting equipment – cranes (type, lifting capacity, lifting speed, control method), lifts (type, lifting capacity).

layout plans of building constructions (layouts, views, cross sections and longitudinal sections),

outlining of the site of individual SO (building structures),

specification and description of the design of technical equipment of buildings (TZB) – medical technology, building low-voltage and high-voltage electrical equipment (including grounding and lightning conductors), heating, ventilation and air conditioning, including their I&C

other data enabling assessment of the level of building constructions

Machinery technology and related equipment

Descriptions, drawings and calculations and other materials, in arrangement into individual PS or DPS, documenting the  technological solution of the work, including

information on

- method of delivery – whether the equipment is to be delivered as a whole or in parts, as a packed unit, etc.

- method of solution and technical parameters of technological systems (delivered within the framework of the given PS/DPS)

- technical parameters of main machines and equipment, which are a part of the concerned technological system, including specification of the data on their construction design, basic characteristics, dimensions and weights.

- Within the framework of this information, the Tenderer shall specify/provide, among other data:

- For the shredder/hydraulic shears

  - times for replacement of main parts of the equipment

- For the boiler

  - type of the feeding equipment including the drawing and decisive dimensions and weights

  - grate type with a description of the grate cooling and distribution of combustion air, including the drawing and decisive dimensions and weights

  - type of the incineration chamber and steam boiler, including the drawing and decisive dimensions and weights

  - area of the heat transfer surfaces of the boiler, heat passage coefficient and clogging coefficient, which were used for their computation

  - type of the slag removal system, including the drawing and decisive dimensions and weights

  - kinds of equipment for cleaning of heat-exchange areas, including parameters and consumptions of auxiliary mediums and basic dimensions

  - description of the hydraulic system

- for the flue gas treatment system

  - chemical composition of all reagents in use, including their consumption, the usage of special reagents not commonly available on the market is precluded

- For pipelines, valves, fittings and accessories

  - total gross weight of pipelines, fittings and accessories arranged according to materials (stainless steel, carbon steel …) and according to the mediums groups (high-pressure steam, etc.)

- quality of the materials used, including reasoning of their selection. This concerns, among other things:

  - materials for internal protection of flue gas ducting systems

  - materials for internal protection of the scrubber

  - flap valves in the flue gas ducting system

  - exchangers of the flue gas / flue gas type

  - pumps and pipelines of suspensions

  - material of the grate

  - materials for storage and mixing tanks of chemicals

  - etc.

- used corrosion and erosion additives for each material group, pipeline, system, etc.

- design of heat and sound insulation (scope of use, characteristic properties including conductivity for heat insulation)

- protection of surfaces (basic data for solution of coating systems which are to be used)

- servo drives delivered within the framework of the technological delivery - manufacturers and types (possible in an alternative manner as well), design

- the scope of equipment of the machinery technology (within the framework of the technological supply) with autonomous means for process control and monitoring, or with other specific equipment

- the lifting devices supplied – number, locations, technical data and description

P&I diagrams for systems of given PS/DPS

layout drawings

dimensional drawings of all components such as TG, air condenser

Instrumentation and Control System (I&C)

Descriptions, drawings and computations and other materials documenting the solution of the I&C delivered within the framework of the work, including

information on

- overall configuration of the EVO control system – a detailed description and configuration scheme including DCS as well as autonomous means for the process control supplied within the framework of technological deliveries, including their mutual links, means for contacts with operators …

- manufacturers and types of technical means used (alternative solution being possible), including the means for solution of specific functions, such as TG regulation and protection, measurement of TG vibrations and shifts, overspeed protection of TG, automatic system for oil burners, emission measurement system

- types and parameters of communication between individual elements and levels of the control system

- manner of solution of external links of the control system to the equipment supplied by the contractor within the framework of the technology or electrical devices, including types and parameters of communication where they are used

- manner of solution of external links of the control system to the relating systems and networks outside the limits of the work

- redundancy rate used

- design and equipment of the workplace for contacts with operators, extent and manner of assurance of the local control of individual motors and servodrives

- regulation servodrives - manufacturers and types (alternative solution being possible), design

- sensors supplied - manufacturers and types (alternative solution being possible), design, manner of connection to the system, power supply, diagnostics, calibration method …

- operation camera system supplied – parameters, scope of use, manner of visualisation and archiving

- Documentation of SIL2 (SIL3 – TG overspeed protection) certification for the offered turbine control system.

- SW supplied, number of licences

- layout of the main I&C components – Workplace for operator interface, automation stations, input and output modules, …

Electrical equipment

Descriptions, drawings and computations and other materials documenting the solution of the electrical part of the work, including

information on

- overall solution of electrical equipment – detailed description, single-pole chart, including uninterrupted power supply

- manufacturers and types (alternative solution being possible), parameters, designs and equipment of main items of electrical equipment (especially the generator, generator switch, diesel generator set, transformer and their components, 6 kV switchboards, 0.4 kV switchboards, 22 kV switching station, electrical protections, frequency changers, inverters, DC/DC changers, accumulator batteries)

- dimensions and weights of heavy pieces (especially generator, transformers)

- manner of solution of external links of the electrical equipment supplied, with regard to the networks, and the equipment linked to the work

- layout of the main electrical equipment components (especially the generator, 6kV switchboards, transformers, protection boxes, energising and phasing systems)

- solution of electrical protections of the block: generator + outlet transformer (including list of phasing places)

- materials of cores and insulation of the delivered cables

- number and output data of the most important electrical consumers, including the list of consumers powered from the frequency changers and the list of consumers requiring uninterrupted power supply

List of Departures from Requirements in the Procurement Documents

The list of departures will be prepared in accordance with the instructions for the elaboration of Volume C13 - point 5 above.

Catalogues of firms

In a special file designated Annex 2 to Enclosure 13, catalogues of the offered items of equipment with their technical data will be submitted exclusively with the original of the tender and copy 1 of the tender.

Questionnaires

The participant shall fill in and hand over as a separate Annex 1 to Enclosure 13 the below specified questionnaires elaborated by the contracting authority:

Note:

Data and information stated in the questionnaires need not be repeated in parts 1-6 of Volume 13 – this may be resolved by referencing the questionnaires.

- ANNEX 1 - QUESTIONNAIRES

- Mechanical-technological process systems

## PS 01– Waste processing technology

| Waste processing technology - PS 01 |  |  |
| --- | --- | --- |
| Waste receipt and record – Scales room - DPS 01.01 |  |  |
| Parameter | Unit | Value / data/ information |
| Vehicle scale – entry | items |  |
| Vehicle scale – exit | items |  |
| Weighing capacity for both scales | tonnes |  |
| Weighing precision | kg |  |
| Detection system for identification of radioactive materials | - |  |
| Weighing principle/type of sensors | - |  |
| Manufacturer/Supplier of bridge scales | - |  |
| Manufacturer/Supplier of weighing system (HW + SW) | - |  |
| Weighbridge dimensions | m x m | x |
| Manufacturer of radioactivity detection system | - |  |
| Waste handling, treatment and storage - DPS 01.02 |  |  |
| Cranes – the waste bunker |  |  |
| Parameter | Unit | Value / data/ information |
| Number of cranes | items |  |
| Manufacturer | - |  |
| Minimum transport capacity of the crane | t/h |  |
| Maximum crane travel speed | m/s |  |
| Maximum crab travel speed | m/s |  |
| Maximum grab lift speed | m/s |  |
| Type of the grab | - |  |
| Minimum content of the grab (closed) | m3 |  |
| Number of grab arms | items |  |
| Bulk weight of waste in the grab | kg/m3 |  |
| Gauge of the crane bridge (approx.) | mm |  |
| Maximum lift (approx.) | mm |  |
| Crane rails length (approx.) | mm |  |
| Method of power supply of cranes | - |  |
| Type of engines | - |  |
| Degree of protection according to ČSN | - |  |
| Weighing range of the crane scales | t |  |
| Accuracy of the crane scales | ± kg |  |
| Shredder of large-volume waste with accessories |  |  |
| Shredder |  |  |
| Parameter | Unit | Value / data/ information |
| Shredder type | - |  |
| Drive type | - |  |
| Shredder capacity at the voluminous weight of approx. 0.1 t/m3 | t/h |  |
| Shredder width | mm |  |
| Shredder hopper dimensions | mm x mm |  |
| Annual operation time | h/year |  |
| Electric power of the shredder | kW |  |
| Total weight of the shredder | t |  |
| Conveyor |  |  |
| Parameter | Unit | Value / data/ information |
| Drive type | - |  |
| Length | mm |  |
| Width | mm |  |
| Angle | grad |  |
| Speed | m/min |  |
| Electrical power input of the conveyor | kW |  |
| Conveyor weight | kg |  |
| Lifting equipment (crane) |  |  |
| Parameter | Unit | Value / data/ information |
| Load bearing capacity | t |  |
| Travel type | - |  |
| Lifting speed | m/min |  |
| Manner of control | - |  |
| Waste incineration, boiler with accessories - DPS 01.03 |  |  |
| Equipment for dispensing of waste |  |  |
| Hopper |  |  |
| Parameter | Unit | Value / data/ information |
| Hopper volume | m3 |  |
| Hopper material | - |  |
| Dimensions (w x d x h) | m | x x |
| Wall thickness | mm |  |
| Hopper wall angle to horizontal | grad |  |
| Shut-off flap with hydraulic drive |  |  |
| Parameter | Unit | Value / data/ information |
| Flap type | - |  |
| Drive | - |  |
| Flap dimensions (w x h) | mm x mm | x |
| Height above the feeding table | mm |  |
| Waste shaft |  |  |
| Parameter | Unit | Value / data/ information |
| Shaft dimensions (upper edge (w x l) | m x m | x |
| Shaft dimensions (lower edge (w x l) | m x m | x |
| Shaft depth | m |  |
| Material | - |  |
| Wall thickness | mm |  |
| Shaft wall angle to horizontal | grad |  |
| Method of measuring waste height in the shaft | - |  |
| Cooling equipment |  |  |
| Parameter | Unit | Value / data/ information |
| Cooling water flow (closed system) | l/s |  |
| Inlet temperature | °C |  |
| Outlet temperature | °C |  |
| Cooling method | - | Internal cooling circuit |
| Waste feeder |  |  |
| Parameter | Unit | Value / data/ information |
| Feeder type | - |  |
| Feeder material | - |  |
| Total height of the feeder | mm |  |
| Feeder width | mm |  |
| Feeder travel length | mm |  |
| Feeder speed | mm/min |  |
| Reverse run speed of the feeder | mm/min |  |
| Number of strokes | min-1. |  |
| Drive | - |  |
| Speed control range | mm/min | - |
| Hydraulic unit power input | kW |  |
| Grate |  |  |
| Grate system |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Grate dimensions (w x h) | m x m | x |
| Grate angle | grad |  |
| Number of grate tracks | items |  |
| Track dimensions (w x h) | m x m | x |
| Grate bar dimensions (w x h) | mm x mm | x |
| Number of grate bar rows on one track | items |  |
| Number of grate bars in one row | items |  |
| Number of movable rows | items |  |
| Number of fixed rows | items |  |
| Total number of grate bars | items |  |
| Material of the grate bars | - |  |
| Thermal load of the grate (at 52.1 MW) | kW/m2 |  |
| Thermal load of the grate (at 57.31 MW) | kW/m2 |  |
| Surface temperature of the grate in the combustion zone | °C |  |
| Mechanical load of the grate (with waste throughput of 18.75 t/h) | kg/m2 |  |
| Free area of the grate (air outlet) | m2 |  |
| Total area of the grate | m2 |  |
| Air-cooled area of grate | m2 |  |
| Water-cooled area of grate (if applicable) | m2 |  |
| Total weight of the grate | t |  |
| Grate drive method | - |  |
| Minimum speed of grate motion | mm/s |  |
| Maximum speed of grate motion | mm/s |  |
| Minimum time of grate unloading | min. |  |
| Maximum amount of waste on the grate | t |  |
| Minimum amount of waste on the grate | t |  |
| Average time of waste on the grate | min. |  |
| Pressure loss of the grate without waste | Pa |  |
| Number of zones for primary air supply | items |  |
| Pressure in individual zones |  |  |
| Zone 1 | Pa |  |
| Zone 2 | Pa |  |
| Zone 3 | Pa |  |
| Zone 4 | Pa |  |
| Zone 5 | Pa |  |
| Water cooling of the grate (if applicable) |  |  |
| Parameter | Unit | Value / data/ information |
| Cooling water flow (closed system) | l/s |  |
| Inlet temperature | °C |  |
| Outlet temperature | °C |  |
| Cooling method | - | Internal cooling circuit |
| Hydraulic station for feeding equipment, grate and shut-off flap |  |  |
| Parameter | Unit | Value / data/ information |
| Type | items |  |
| Content of common oil tank | l |  |
| Hydraulic station engine output | kW |  |
| Pump capacity | l/s |  |
| Pressure | MPa |  |
| Water cooling of the hydraulic station |  |  |
| Parameter | Unit | Value / data/ information |
| Cooling water flow (closed system) | l/s |  |
| Inlet temperature | °C |  |
| Outlet temperature | °C |  |
| Cooling method | - | Internal cooling circuit |
| Incineration chamber with brick lining |  |  |
| Arrangement of the incineration chamber |  |  |
| Parameter | Unit | Value / data/ information |
| Volume of the incineration chamber | m3 |  |
| Depth of the incineration chamber | mm |  |
| Width of the incineration chamber | mm |  |
| Height of the incineration chamber | mm |  |
| Specific heat load of the incineration chamber at 52.1 MW | kW/m3 |  |
| Specific heat load of the incineration chamber at 57.31 MW | kW/m3 |  |
| Protection of heat transfer surfaces of the furnace and incineration chamber |  |  |
| Parameter | Unit | Value / data/ information |
| Heat protection rating | °C |  |
| Ceiling of the incineration chamber |  |  |
| Type |  |  |
| Material | - |  |
| Walls of the incineration chamber | - |  |
| Type | - |  |
| Material | - |  |
| Total heat transfer surface in radiation pass | m2 |  |
| Flue gas temperature at inlet to convectional areas of the boiler | °C |  |
| Total area of incineration chamber protection | m2 |  |
| Total height of protection of the incineration chamber from the lower edge of the grate | m |  |
| Brick lining type | - |  |
| Firecrete type | - |  |
| Ceramic board type | - |  |
| Type of anti-corrosive alloy cladding | - |  |
| Brick lining quality | - |  |
| Firecrete quality | - |  |
| Ceramic board quality | - |  |
| Quality of anti-corrosive alloy cladding | - |  |
| Thickness of anti-corrosive alloy cladding | mm |  |
| Area of anti-corrosive alloy cladding | m2 |  |
| Protection fixing method | - |  |
| Studs - material | - |  |
| Stud length | - |  |
| Average | - |  |
| Number of studs | pieces/ m2 |  |
| Distance anchors - material | - |  |
| Number of anchors | pieces/ m2 |  |
| Hooks for ceramic board suspension - material | - |  |
| Number of hooks | pieces/ m2 |  |
| Incineration air system, including incineration regulation |  |  |
| Primary air piping |  |  |
| Parameter | Unit | Value / data/ information |
| Suction piping cross section (waste bunker) | m2 |  |
| Velocity of intake air (suction nozzle) | m/s |  |
| Velocity of intake air (piping) | m/s |  |
| Pipe wall thickness | mm |  |
| Possibility of piping cleaning | - |  |
| Measurement of quantity of intake air | Nm3/h |  |
| Primary air fan |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type (radial fan) | - |  |
| Air quantity | Nm3/h |  |
| Air quantity (max.) | Nm3/h |  |
| Air temperature at the fan outlet | °C |  |
| Total pressure difference | kPa |  |
| Engine input | kW |  |
| Supply voltage | V |  |
| Efficiency | % |  |
| Speed | min-1. |  |
| Temperature downstream of the heater | °C |  |
| Air quantity control | - |  |
| Noise level (1 m) | dB |  |
| One-spar crab | t |  |
| Primary air steam heater – assumption of 3 sections |  |  |
| Parameter | Unit | Value / data/ information |
| 1st section - condensate heating |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Nominal pressure (PN 25) | MPa |  |
| Design temperature | °C |  |
| Air quantity | Nm3/h |  |
| Primary air temperature rise by | °C |  |
| Condensate temperature | °C |  |
| 2nd section - steam heating |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Nominal pressure (PN 40) | MPa |  |
| Design temperature | °C |  |
| Air quantity | Nm3/h |  |
| Primary air temperature rise by | °C |  |
| Emission steam temperature | °C |  |
| Steam pressure | MPa |  |
| 3rd section - heating by high-pressure superheated steam (boiler exit) |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Nominal pressure (PN 100) | MPa |  |
| Design temperature | °C |  |
| Air quantity | Nm3/h |  |
| Primary air temperature rise by | °C |  |
| Steam temperature | °C |  |
| Steam pressure | MPa |  |
| Total weight of the steam heater | kg |  |
| Side air |  |  |
| Parameter | Unit | Value / data/ information |
| Side air piping |  |  |
| Intake piping cross section | m2 |  |
| Velocity of intake air (suction nozzle) | m/s |  |
| Velocity of intake air (piping) | m/s |  |
| Pipe wall thickness | mm |  |
| Possibility of piping cleaning | - |  |
| Measurement of quantity of intake air | - |  |
| Side air fan |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type (radial fan) | - |  |
| Air quantity | Nm3/h |  |
| Air quantity (max.) | Nm3/h |  |
| Air temperature at the fan outlet | °C |  |
| Total pressure difference | kPa |  |
| Power input | kW |  |
| Efficiency | % |  |
| Speed | min-1. |  |
| Air quantity control | - |  |
| Noise level (1 m) | dB |  |
| One-spar crab | t |  |
| Secondary air |  |  |
| Parameter | Unit | Value / data/ information |
| Secondary air piping |  |  |
| Intake piping cross section | m2 |  |
| Velocity of intake air (suction nozzle) | m/s |  |
| Velocity of intake air (piping) | m/s |  |
| Pipe wall thickness | mm |  |
| Possibility of piping cleaning | - |  |
| Measurement of quantity of intake air | - |  |
| Secondary air fan |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type (radial fan) | - |  |
| Air quantity | Nm3/h |  |
| Air quantity (max.) | Nm3/h |  |
| Air temperature at the fan outlet | °C |  |
| Total pressure difference | kPa |  |
| Power input | kW |  |
| Efficiency | % |  |
| Speed | min-1. |  |
| Air quantity control | - |  |
| Noise level (1 m) | dB |  |
| One-spar crab | t |  |
| Flue gas recirculation |  |  |
| Recirculated flue gas piping |  |  |
| Parameter | Unit | Value / data/ information |
| Intake piping cross section | m2 |  |
| Velocity of intake flue gas (suction nozzle) | m/s |  |
| Velocity of intake flue gas (piping) | m/s |  |
| Pipe wall thickness | mm |  |
| Possibility of piping cleaning | - |  |
| Measurement of quantity of intake air | - |  |
| Recirculated flue gas fan |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type (radial fan) | - |  |
| Recirculated flue gas quantity | Nm3/h |  |
| Recirculated flue gas quantity (max.) | Nm3/h |  |
| Recirculated flue gas temperature at the fan outlet | °C |  |
| Total pressure difference | kPa |  |
| Power input | kW |  |
| Efficiency | % |  |
| Speed | min-1. |  |
| Recirculated flue gas quantity control | - |  |
| Noise level (1 m) | dB |  |
| One-spar crab | t |  |
| Ignition and stabilisation of incineration (burners) |  |  |
| Parameter | Unit | Value / data/ information |
| Burner manufacture | - |  |
| Number of burners | items |  |
| Type | - |  |
| Burner output | MW |  |
| Fuel value | MJ/Nm3 |  |
| Fuel consumption - natural gas | Nm3/h |  |
| Output regulation range | MW |  |
| Burner control | - |  |
| Ignition method | - |  |
| Flame control | - |  |
| Burner body material | - |  |
| Combustion air | Nm3/h |  |
| Burner cooling air | Nm3/h |  |
| Noisiness | dB |  |
| Recuperation of heat | % |  |
| Electrical power input | kW |  |
| Special properties (e.g. NOx reduction) | - |  |
| Total weight | kg |  |
| Steam boiler with accessories |  |  |
| Boiler |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Boiler type | - |  |
| Operating pressure | MPa |  |
| Design pressure | MPa |  |
| Flue gas temperature for a dirty boiler (8000 hours) |  |  |
| Upstream of the inlet convection evaporator | °C |  |
| Upstream of the superheater 3 | °C |  |
| Downstream of the superheater 3 | °C |  |
| Downstream of the superheater 2 | °C |  |
| Downstream of the superheater 1 | °C |  |
| Downstream of the evaporator 3 | °C |  |
| Downstream of the evaporator 2 | °C |  |
| Downstream of the evaporator 1 | °C |  |
| Downstream of the economizer 3 | °C |  |
| Downstream of the economizer 2 | °C |  |
| Downstream of the economizer 1 | °C |  |
| Areas of heat transfer surfaces |  |  |
| Parameter | Unit | Value / data/ information |
| 1st pass - to turn to the 2nd pass | m2 |  |
| Grill between 1st and 2nd passes | m2 |  |
| 2nd pass - to turn to the 3rd pass | m2 |  |
| 3rd pass – to boiler horizontal part entry | m2 |  |
| Walls of the 4th pass | m2 |  |
| Total radiation area | m2 |  |
| Inlet evaporator | m2 |  |
| Superheater 3 | m2 |  |
| Superheater 2 | m2 |  |
| Superheater 1 | m2 |  |
| Evaporator 3 | m2 |  |
| Evaporator 2 | m2 |  |
| Evaporator 1 | m2 |  |
| Economizer 3 | m2 |  |
| Economizer 2 | m2 |  |
| Economizer 1 | m2 |  |
| Total convection area | m2 |  |
| Total heat transfer surfaces of the boiler | m2 |  |
| Boiler drum |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | - |  |
| External diameter | mm |  |
| Wall thickness | mm |  |
| Length of the cylindrical part | mm |  |
| Material | - |  |
| Total volume | m3 |  |
| Volume of the steam chamber | m3 |  |
| Drift eliminator design |  |  |
| Evaporation area | m2 |  |
| Total weight | kg |  |
| Passage between pipes of individual convection areas |  |  |
| Parameter | Unit | Value / data/ information |
| Grill between 1st and 2nd passes | mm |  |
| Inlet evaporator | mm |  |
| Superheater 3 | mm |  |
| Superheater 2 | mm |  |
| Superheater 1 | mm |  |
| Evaporator 3 | mm |  |
| Evaporator 2 | mm |  |
| Evaporator 1 | mm |  |
| Economizer 3 | mm |  |
| Economizer 2 | mm |  |
| Economizer 1 | mm |  |
| Safety valve downstream of the superheater |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | - |  |
| Type | items |  |
| Throughput for the safety valve | kg/s |  |
| Opening speed | s |  |
| Opening overpressure | MPa |  |
| Noise suppressor | - |  |
| Safety valve of the boiler drum |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | - |  |
| Type | items |  |
| Throughput for the safety valve | kg/s |  |
| Opening speed | s |  |
| Opening overpressure | MPa |  |
| Noise suppressor | - |  |
| Atmospheric expander |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | - |  |
| Boiler feed water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Feed water tank volume | m3 |  |
| Operating pressure | MPa |  |
| Operating temperature (max.) | °C |  |
| Tank material | - |  |
| Total weight of the tank (without water) | kg |  |
| Boiler feed water pumps |  |  |
| Parameter | Unit | Value / data/ information |
| Number of feed water pumps | items |  |
| Pump drive | - |  |
| Capacity control | l/s | - |
| Pump type | - |  |
| Manufacturer | - |  |
| Pump efficiency in working point | % |  |
| Outlet pressure | MPa |  |
| Pump flow rate | l/s |  |
| Pumped liquid temperature | °C |  |
| Pumps of supply of demineralized water from the demineralized water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Number of feed water pumps | items |  |
| Pump drive | - |  |
| Capacity control | l/s | - |
| Pump type | - |  |
| Manufacturer | - |  |
| Pump efficiency in working point | % |  |
| Outlet pressure | MPa |  |
| Pump flow rate | l/s |  |
| Pumped liquid temperature | °C |  |
| Demineralized water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Feed water tank volume | m3 |  |
| Operating pressure | MPa |  |
| Operating temperature (max.) | °C |  |
| Tank material | - |  |
| Total weight of the tank (without water) | kg |  |

| Waste processing technology - PS 01 |  |  |
| --- | --- | --- |
| Condensate piping from the turbine condenser to boiler feed water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Min. pressure | MPa |  |
| Min. temperature | °C |  |
| Nominal inside diameter | DN: |  |
| Pressure nominal | MPa |  |
| External diameter | mm |  |
| Wall thickness | mm |  |
| Material | - |  |
| Number of valves | items |  |
| Condensate piping from the heating water heater to boiler feed water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Min. pressure | MPa |  |
| Min. temperature | °C |  |
| Nominal inside diameter | DN: |  |
| Pressure nominal | MPa |  |
| External diameter | mm |  |
| Wall thickness | mm |  |
| Material | - |  |
| Number of valves | items |  |
| Demineralized water piping to boiler feed water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Min. pressure | MPa |  |
| Min. temperature | °C |  |
| Nominal inside diameter | DN: |  |
| Pressure nominal | MPa |  |
| External diameter | mm |  |
| Wall thickness | mm |  |
| Material | - |  |
| Number of valves | items |  |
| Dispensing of chemicals |  |  |
| Parameter | Unit | Value / data/ information |
| Automatic station manufacturer | - |  |
| Supply voltage | V |  |
| Medium 1 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Drive | - |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Medium 2 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Drive |  |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Medium 3 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Drive | - |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Denox |  |  |
| Parameter | Unit | Value / data/ information |
| Driving medium type | - |  |
| Driving medium consumption | kg/h |  |
| Water consumption | m3/h |  |
| Pressure air consumption | m3/h |  |
| Electric input | kW |  |
| Reduction factor | % |  |
| Ammonia water consumption (as 25%-NH3) | kg/h |  |
| Specific consumption of NH3 in kg NH3 / kg NO2 | kg / kg |  |
| Specific consumption of NH3 in kg NH3 / ton of waste | kg/t |  |
| Stoichiometric factor |  |  |
| Content of ammonia in flue gases (at 11 vol. % O2, dry) | mg/Nm3 |  |
| Reducing agent injection system |  |  |
| Parameter | Unit | Value / data/ information |
| Number of injection nozzles | items |  |
| Number of injection levels | number |  |
| Nozzle type | - |  |
| Nozzle dimension | mm | x |
| Nozzle material | mat. no. |  |
| Mixing chamber of the driving medium and reducing agent | type |  |
| Control method | - |  |
| Ammonia water storage tank |  |  |
| Parameter | Unit | Value / data/ information |
| Tank volume | m3 |  |
| Tank dimensions Ø x d | m x m | x |
| Tank wall thickness | mm |  |
| Tank material | mat. no. |  |
| Empty tank weight | t |  |
| Full tank weight | t |  |
| Ammonia water pumping |  |  |
| Parameter | Unit | Value / data/ information |
| Tank refilling pump | - |  |
| Dosing pumps |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Type | items |  |
| - of this standby ones | items |  |
| Pumping rate | l/s |  |
| Pumping head | m |  |
| Pump power input | kW |  |
| Pump casing material | mat. no. |  |
| Piping material | mat. no. |  |
| Valve material | mat. no. |  |
| Pump weight including motor | kg |  |
| Slag removal system |  |  |
| Slag production |  |  |
| Parameter | Unit | Value / data/ information |
| Yearly production | t |  |
| Number of belt conveyors | items |  |
| Transport capacity | t/h |  |
| Length | m |  |
| Power output | kW |  |
| Manufacturer | - |  |
| Slag separator shaft |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Shaft dimensions: w x l x d | m | x x |
| Slag removal shaft material | mat. no. |  |
| Wear protection material | mat. no. |  |
| Slag removal unit tub with arm-type carrier |  |  |
| Parameter | Unit | Value / data/ information |
| Slag throughput | t/h |  |
| Inlet opening cross section w x d | mm | x |
| Outlet opening cross section w x d | mm | x |
| Tub dimensions: w x l x h | mm | x x |
| Water volume | m3 |  |
| Slag removal tub material | mat. no. |  |
| Tub wall thickness | mm |  |
| Wear protection thickness | mm |  |
| Wear protection material | mat. no. |  |
| Operation mode |  |  |
| Engine output | kW |  |
| Transport speed of the slag removal system | m/min |  |
| Conveyor to slag bunker |  |  |
| Parameter | Unit | Value / data/ information |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Exhaust of vapours |  |  |
| Parameter | Unit | Value / data/ information |
| Dimensions of filtering bell of the slag-removing plant: w x d | mm | x |
| Dimensions of filtering bell of slag bunker: w x d | mm | x |
| Adapter material | mat. no. |  |
| Scavenge pipe material | mat. no. |  |
| Scavenge pipe cross section | mm |  |
| Vapour exhaust method | - |  |
| Vapour exhaust fan | type |  |
| Insulation Minimum thickness of insulation layer |  |  |
| Parameter | Unit | Value / data/ information |
| Boiler | mm |  |
| Boiler drum | mm |  |
| Piping of HP superheated steam | mm |  |
| Feed water tank | mm |  |
| Feeding water (condensate) pipeline | mm |  |
| Insulation against condensed water | mm |  |
| Bleeder on the HP superheated steam side | mm |  |
| Demineralized water tank | mm |  |
| Demineralized water pipeline | mm |  |
| Insulation type |  |  |
| Parameter | Unit | Value / data/ information |
| Boiler | - |  |
| Boiler drum | - |  |
| Piping of HP superheated steam | - |  |
| Feed water tank | - |  |
| Feeding water (condensate) pipeline | - |  |
| Insulation against condensed water | - |  |
| Bleeder on the HP superheated steam side | - |  |
| Demineralized water tank | - |  |
| Demineralized water pipeline | - |  |
| Flue gas treatment - DPS 01.04 |  |  |
| Electrostatic separator |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Number of sections | number |  |
| Free cross section | m2 |  |
| Max. speed of flue gas | m/s |  |
| Time of presence in the active space | s |  |
| Section height | m |  |
| Total length of section 1 | m |  |
| Total length of section 2 | m |  |
| Total length of section 3 | m |  |
| Number of hoppers | items |  |
| Sheet thickness of input and output parts | mm |  |
| Sheet thickness of electrostatic separator box | mm |  |
| Sheet thickness of hoppers | mm | 5 |
| Insulation sheet thickness | mm |  |
| Thickness of insulation of input and output parts | mm |  |
| Thickness of insulation of the electrostatic separator box | mm |  |
| Thickness of insulation of hoppers | mm |  |
| Total weight of the electrostatic separator | t |  |
| Electric equipment |  |  |
| Parameter | Unit | Value / data/ information |
| Number of HV sources | items |  |
| Source current | mA rms |  |
| Peak voltage | kV |  |
| Power input | kVA |  |
| Electric output: |  |  |
| Hopper heating | kW |  |
| Unloading screw conveyors | kW |  |
| Turnstile gates | kW |  |
| Knocking system |  |  |
| Parameter | Unit | Value / data/ information |
| Knocking of HV electrodes | items |  |
| Knocking of passive electrodes | items |  |
| Knocking of insulators | items |  |
| Noise level at 1.5 m | dB(A) |  |
| Insulator heating |  |  |
| Parameter | Unit | Value / data/ information |
| Type | items |  |
| Power output | kW |  |
| Catalytic filter |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Total filtration area | m2 |  |
| Active filtration area in operation | m2 |  |
| Washed area in operation | m2 |  |
| Number of filtration hoses | items |  |
| Filtration hose diameter | mm |  |
| Filtration hose length | m |  |
| Number of hoppers | items |  |
| Sheet thickness of input and output parts | mm |  |
| Sheet thickness of catalytic filter box | mm |  |
| Sheet thickness of hoppers | mm |  |
| Insulation sheet thickness | mm |  |
| Thickness of insulation of input and output parts | mm |  |
| Thickness of insulation of the catalytic filter box | mm |  |
| Thickness of insulation of hoppers | mm |  |
| Total weight of the catalytic filter | t |  |
| Dusting agent | - |  |
| Dusting agent container | m3 |  |
| Dusting method | - |  |
| Flue gas ducts |  |  |
| Ducting between the boiler and the electrostatic separator |  |  |
| Parameter | Unit | Value / data/ information |
| Length | m |  |
| Cross section | m2 |  |
| Wall thickness | mm |  |
| Flue gas flow rate in the ducting at constant output | m/s |  |
| Material | - |  |
| Noise suppression | dB |  |
| Compensators - type |  |  |
| Compensators - number | items |  |
| Connection type |  |  |
| Insulation sheet thickness | mm |  |
| Insulation thickness | mm |  |
| Ducting between the electrostatic separator and the catalytic filter |  |  |
| Parameter | Unit | Value / data/ information |
| Length | m |  |
| Cross section | m2 |  |
| Wall thickness | mm |  |
| Flue gas flow rate in the ducting at constant output | m/s |  |
| Material | - |  |
| Noise suppression | - |  |
| Compensators - type | - |  |
| Compensators - number | items |  |
| Connection type | - |  |
| Insulation sheet thickness | mm |  |
| Insulation thickness | mm |  |
| Ducting between the catalytic filter and the flue gas scrubber |  |  |
| Parameter | Unit | Value / data/ information |
| Length | m |  |
| Cross section | m2 |  |
| Wall thickness | mm |  |
| Flue gas flow rate in the ducting at constant output | m/s |  |
| Material | - |  |
| Noise suppression | - |  |
| Compensators - type | - |  |
| Compensators - number | items |  |
| Connection type | - |  |
| Insulation sheet thickness | mm |  |
| Insulation thickness | mm |  |
| Ducting between the flue gas scrubber and the fan |  |  |
| Parameter | Unit | Value / data/ information |
| Length | m |  |
| Cross section | m2 |  |
| Wall thickness | mm |  |
| Flue gas flow rate in the ducting at constant output | m/s |  |
| Material | - |  |
| Noise suppression | - |  |
| Compensators - type | - |  |
| Compensators - number | items |  |
| Connection type | - |  |
| Insulation sheet thickness | mm |  |
| Insulation thickness | mm |  |
| Ducting between the flue gas fan and the stack |  |  |
| Parameter | Unit | Value / data/ information |
| Length | m |  |
| Cross section | m2 |  |
| Wall thickness | mm |  |
| Flue gas flow rate in the ducting at constant output | m/s |  |
| Material | - |  |
| Noise suppression | - |  |
| Compensators - type | - |  |
| Compensators - number | items |  |
| Connection type | - |  |
| Insulation sheet thickness | mm |  |
| Insulation thickness | mm |  |
| Scrubber flue gas |  |  |
| Pumps of the 1st stage of the scrubber |  |  |
| Parameter | Unit | Value / data/ information |
| Type | items |  |
| Drive | - |  |
| Manufacturer | - |  |
| Pump efficiency in working point | % |  |
| Pump capacity | l/s |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Pumps of the 2nd stage of the scrubber |  |  |
| Parameter | Unit | Value / data/ information |
| Type | items |  |
| Drive | - |  |
| Manufacturer | - |  |
| Pump efficiency in working point | % |  |
| Pump capacity | l/s |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| NaOH tank |  |  |
| Parameter | Unit | Value / data/ information |
| Tank design | - |  |
| Max. time of tank filling | h |  |
| Volume | m3 |  |
| Dimensions: Ø x h | m |  |
| Wall thickness | mm |  |
| Material | mat. no. |  |
| Corrosion protection | - |  |
| Tank weight | t |  |
| NaOH concentration | % |  |
| Specific consumption of NaOH | l/t of waste |  |
| Emergency water tank |  |  |
| Parameter | Unit | Value / data/ information |
| Max. time of tank filling | h |  |
| Volume | m3 |  |
| Dimensions: Ø x h | m |  |
| Wall thickness | mm |  |
| Material | mat. no. |  |
| Corrosion protection | - |  |
| Tank weight | t |  |
| Flue way pressure loss |  |  |
| Parameter | Unit | Value / data/ information |
| Pressure loss of the boiler (up to boiler outlet) | mbar |  |
| Pressure loss from the boiler outlet to electric filter outlet | mbar |  |
| Pressure loss from electric filter outlet to catalytic filter outlet | mbar |  |
| Pressure loss of flue gas ducting from catalytic filter to flue gas scrubber inlet | mbar |  |
| Pressure loss of the flue gas scrubber | mbar |  |
| Pressure loss of the flue gas ducting from flue gas scrubber outlet to flue gas fan inlet | mbar |  |
| Pressure loss of the flue gas from the flue gas fan outlet to the stack inlet | mbar |  |
| Pressure loss of the stack | mbar |  |
| Reserve | mbar |  |
| Total pressure loss | mbar |  |
| Flue gas fan |  |  |
| Parameter | Unit | Value / data/ information |
| Fan speed | min-1. |  |
| Fan efficiency | % |  |
| Engine efficiency | % |  |
| Total efficiency | % |  |
| Power input, total | kW |  |
| Engine output | kW |  |
| Voltage | V |  |
| Engine ingress protection | IP |  |
| Noise level with insulation | dB(A) |  |
| Fan manufacturer | - |  |
| Engine manufacturer | - |  |
| Fan type | - |  |
| Sheet thickness | mm |  |
| Wheel type | - |  |
| Fan spindle mounting | - |  |
| Spindle sealing type | - |  |
| Sound insulation type | - |  |
| Heat insulation type | - |  |
| Power control method | - |  |
| Vibration control | - |  |
| Control of temperature rise of engine winding | - |  |
| Regulation range | min-1. |  |
| Weight of the fan and engine | kg |  |

## Turbo-generator - PS 02

| Turbo-generator - PS 02 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Turbine |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Manufacturer | - |  |  |  |
| Type | - |  |  |  |
| Nominal output | MW |  |  |  |
| Number of casings | items |  |  |  |
| Overload capacity | % |  |  |  |
| Nominal speed | min-1. |  |  |  |
| Nominal operation flow | t.h-1 |  |  |  |
| Maximum operation flow | t.h-1 |  |  |  |
| Steam pressure upstream of the quick-closing valve: |  |  |  |  |
| - nominal | MPaabs |  |  |  |
| - maximum | MPaabs |  |  |  |
| Steam temperature upstream of the quick-closing valve: |  |  |  |  |
| - nominal | °C |  |  |  |
| - maximum | °C |  |  |  |
| Steam pressure in the 1st regulated extraction at nominal output | MPa |  |  |  |
| Steam temperature in the 1st regulated extraction at nominal output | °C |  |  |  |
| Steam quantity in the 1st regulated extraction at nominal output | t/h |  |  |  |
| Number of non-regulated extraction points | items |  |  |  |
| Type of drives of control valves | - |  |  |  |
| Type of drive of quick-closing valve | - |  |  |  |
| Type of drives of extraction flaps | - |  |  |  |
| Regulation type and number of control valves | - / pcs |  |  |  |
| Heat insulation of TG: |  |  |  |  |
| - method of realization of heat insulation of TG | - |  |  |  |
| - insulation material | - |  |  |  |
| Noise insulation of TG: |  |  |  |  |
| - method of realization of noise insulation of TG | - |  |  |  |
| - cover of the entire turbo set incl. generator | Yes/No |  |  |  |
| Weight: |  |  |  |  |
| - complete turbine rotor | kg |  |  |  |
| - complete casing cover | kg |  |  |  |
| - complete casing bottom | kg |  |  |  |
| Extraction flaps of TG (fill in separately for each flap) |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Valve type | - |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | PN |  |  |  |
| Working stage | - |  |  |  |
| Extraction flaps of TG (fill in separately for each flap) |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Valve type | - |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | PN |  |  |  |
| Working stage | - |  |  |  |
| Quick-closing valve of TG |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Valve type | - |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | PN |  |  |  |
| Working stage | - |  |  |  |
| High-pressure hydraulics (HPHR) |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Type | - |  |  |  |
| Tank volume | m3 |  |  |  |
| Working amount of hydraulic fluid | m3 |  |  |  |
| Designation of the hydraulic fluid used | - |  |  |  |
| Nominal output pressure | MPa |  |  |  |
| Accumulator type | - |  |  |  |
| Nominal pressure in the accumulator | MPa |  |  |  |
| HPHR pumps - type | - |  |  |  |
| Number of HPHR pumps | items |  |  |  |
| TG oil tank |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Tank type | - |  |  |  |
| Total volume of the tank | m3 |  |  |  |
| Useful volume | m3 |  |  |  |
| Heating | yes / no |  |  |  |
| Operation storage | m3 |  |  |  |
| Material design | - |  |  |  |
| Level measurement - type | - |  |  |  |
| Corrosion protection | method |  |  |  |
| Total service weight | kg |  |  |  |
| TG lubrication oil system |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Oil type | - |  |  |  |
| Amount of oil for TG - one charge | m3 |  |  |  |
| Nominal pressure of lubricating oil | kPa |  |  |  |
| Minimum pressure of lubricating oil | kPa |  |  |  |
| Maximum pressure of lubricating oil | kPa |  |  |  |
| Oil cooler: |  |  |  |  |
| - manufacturer | - |  |  |  |
| - type | - |  |  |  |
| - number | items |  |  |  |
| - nominal inlet water temperature | °C |  |  |  |
| - maximum inlet water temperature | °C |  |  |  |
| - cooling water consumption at maximum inlet water temperature | t.h-1 |  |  |  |
| - heat transfer surface | m2 |  |  |  |
| - dimensions – depth / width / height | mm/mm/mm |  |  |  |
| - material design | - |  |  |  |
| - total weight of the cooler | kg |  |  |  |
| Duplex filter: |  |  |  |  |
| - manufacturer | - |  |  |  |
| - type | - |  |  |  |
| - filtering capacity | μm |  |  |  |
| Oil temperature regulator: |  |  |  |  |
| - manufacturer | - |  |  |  |
| - type | - |  |  |  |
| Oil pressure regulator: |  |  |  |  |
| - manufacturer | - |  |  |  |
| - type | - |  |  |  |
| Main oil pump: |  |  |  |  |
| Manufacturer | - |  |  |  |
| Delivery head | m |  |  |  |
| Power input | kW |  |  |  |
| Efficiency | % |  |  |  |
| - pump type | - |  |  |  |
| - nominal speed | rpm |  |  |  |
| - speed corresponding to minimum oil pressure | rpm |  |  |  |
| oil flow rate: |  |  |  |  |
| - nominal | m3/h |  |  |  |
| - maximum | m3/h |  |  |  |
| - minimum | m3/h |  |  |  |
| Live steam pipelines |  |  |  |  |
| Parameter | Unit | Value / data/ information |  |  |
| Manufacturer | - |  |  |  |
| Dimensions of the piping from the boiler to TG | mm x mm |  |  |  |
| Piping leak measurement from the boiler to TG | Yes/No |  |  |  |
| Pressure loss between the boiler and TG at nominal flow rate | kPa |  |  |  |
| Maximum admissible steam pressure | MPa |  |  |  |
| Maximum steam temperature | °C |  |  |  |
| Maximum permissible change of the steam temperature | °C/min |  |  |  |
| Method of pipe laying | - |  |  |  |
| Pipeline insulation: | - |  |  |  |
| - material | - |  |  |  |
| - layer thickness | mm |  |  |  |
| - surface finish | - |  |  |  |
| Pipe material | - |  |  |  |
| Pipelines, fittings and valves |  |  |  |  |
| From the boiler superheated steam outlet to the turbine inlet |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Min. pressure | MPa |  |  |  |
| Min. temperature | °C |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | MPa |  |  |  |
| Steam temperature | °C |  |  |  |
| External diameter | mm |  |  |  |
| Wall thickness | mm |  |  |  |
| Length | m |  |  |  |
| Material | - |  |  |  |
| Number of valves | items |  |  |  |
| From the superheated steam piping to the inlet of the 1.72 bar steam pressure reducing station (bypass) |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Min. pressure | MPa |  |  |  |
| Min. temperature | °C |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | MPa |  |  |  |
| Steam temperature | °C |  |  |  |
| External diameter | mm |  |  |  |
| Wall thickness | mm |  |  |  |
| Length | m |  |  |  |
| Material | - |  |  |  |
| Number of valves | items |  |  |  |
| From the superheated steam piping to the inlet of the 1.2 MPa steam pressure reducing station |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Min. pressure | MPa |  |  |  |
| Min. temperature | °C |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | MPa |  |  |  |
| Steam temperature | °C |  |  |  |
| External diameter | mm |  |  |  |
| Wall thickness | mm |  |  |  |
| Length | m |  |  |  |
| Material | - |  |  |  |
| Number of valves | items |  |  |  |
| Distribution piping of 1.72 bar steam |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Min. pressure | bar |  |  |  |
| Min. temperature | °C |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | MPa |  |  |  |
| Steam temperature | °C |  |  |  |
| External diameter | mm |  |  |  |
| Wall thickness | mm |  |  |  |
| Length | m |  |  |  |
| Material | - |  |  |  |
| Number of valves | items |  |  |  |
| Distribution piping of 1.2 MPa steam for technological purposes |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Min. pressure | MPa |  |  |  |
| Min. temperature | °C |  |  |  |
| Nominal inside diameter | DN: |  |  |  |
| Pressure nominal | MPa |  |  |  |
| Steam temperature | °C |  |  |  |
| External diameter | mm |  |  |  |
| Wall thickness | mm |  |  |  |
| Length | m |  |  |  |
| Material | - |  |  |  |
| Number of valves | items |  |  |  |
| Gearbox |  |  |  |  |
| Type | - |  |  |  |
| Manufacturer of gearbox | - |  |  |  |
| Nominal power output | kW |  |  |  |
| Gear ratio | - |  |  |  |
| Number of speed gears | number |  |  |  |
| Input speed | min-1. |  |  |  |
| Output speed | min-1. |  |  |  |
| Cooling | - |  |  |  |
| Lubrication | - |  |  |  |
| Total weight | kg |  |  |  |
| Electric generator |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Type | - |  |  |  |
| Generator manufacturer | - |  |  |  |
| Nominal power output | kW |  |  |  |
| Nominal voltage of the generator | V |  |  |  |
| Nominal speed | min-1. |  |  |  |
| Nominal frequency | Hz |  |  |  |
| Nominal power factor | cos φ |  |  |  |
| Efficiency at nominal output cos φ 0.8 | % |  |  |  |
| Efficiency at nominal output cos φ 1.0 | % |  |  |  |
| Efficiency at 50% output cos φ 0.8 | % |  |  |  |
| Efficiency at 50% output cos φ 1.0 | % |  |  |  |
| Generator exciter - type | - |  |  |  |
| Excitation set - type | - |  |  |  |
| No-load excitation voltage | V |  |  |  |
| Nominal excitation voltage | V |  |  |  |
| No-load excitation current | A |  |  |  |
| Nominal excitation current | A |  |  |  |
| Phase connection | - |  |  |  |
| Number of outlets | - |  |  |  |
| Moment of inertia | kgm2 |  |  |  |
| Short-circuit torque moment | Nm |  |  |  |
| Short-circuit moment to foundation | Nm |  |  |  |
| Method of generator cooling according to ČSN EN 60034-6 | - |  |  |  |
| Degree of protection according to ČSN EN 60034-5-ed.3 | IP |  |  |  |
| Generator shape per ČSN EN 60034-7 + A1 | - |  |  |  |
| Thermal output at nominal load | kW |  |  |  |
| Noise level according to ČSN EN 60034-9-ed.2 | - |  |  |  |
| Winding insulation class | - |  |  |  |
| Sense of rotation per ČSN EN 60034 -8 ed. 2 2 | - |  |  |  |
| Total weight of the generator | kg |  |  |  |
| Weight of the turbine platform without concrete element | t |  |  |  |
| Building volume of concrete supporting structure | m3 |  |  |  |
| Electric turning gear |  |  |  |  |
| Manufacturer | - |  |  |  |
| Type | - |  |  |  |
| Power input | kW |  |  |  |
| Output speed | min-1. |  |  |  |
| Weight: | kg |  |  |  |
| Steam reduction station – turbine bypass |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Max. amount of inlet steam (4.2 MPa) | t/h |  |  |  |
| Inlet steam pressure | MPa |  |  |  |
| Inlet steam temperature | °C |  |  |  |
| Consumption of feeding water for spray | t/h |  |  |  |
| Steam pressure on the outlet (regulated)* | MPa |  |  |  |
| Steam temperature on the outlet (regulated)* | °C |  |  |  |
| Regulation range from ... to | % |  |  | - |
| Cooling water temperature at max. output | t/h |  |  |  |
| Cooling water temperature at 50% output | t/h |  |  |  |
| Cooling water temperature at 25% output | t/h |  |  |  |
| Weight of complete pressure reducing station | t |  |  |  |
| Pressure reducing station of steam - for technological purposes |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Maximum amount of steam | t/h |  |  |  |
| Inlet steam pressure | MPa |  |  |  |
| Inlet steam temperature | °C |  |  |  |
| Outlet pressure of technological steam | MPa |  |  |  |
| Outlet temperature of technological steam | °C |  |  |  |
| Consumption of feeding water for spray | t/h |  |  |  |
| Turbine hall crane |  |  |  |  |
| Parameter | Unit |  |  | Value / data/ information |
| Crane manufacturer |  |  |  |  |
| Crane load bearing capacity | t |  |  |  |
| Crane rails length | m |  |  |  |
| Bridge travel speed | m/min |  |  |  |
| Crab travel speed | m/min |  |  |  |
| Lifting speed | m/min |  |  |  |
| Bridge travel engine output | kW |  |  |  |
| Crab travel engine output | kW |  |  |  |
| Precise lifting device engine output | kW |  |  |  |
| Crane control | - |  |  |  |
| Crane bridge with the drive | t |  |  |  |
| Crab with the drive | t |  |  |  |
| Lifting device with the drive, hauling rope and hooks | t |  |  |  |
| Total weight of the crane | t |  |  |  |

## Condensation, cooling PS - 03

| Condensation, cooling PS - 03 |  |  |
| --- | --- | --- |
| Surface condenser |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type / number of draughts | - / - |  |
| Overall dimensions: |  |  |
| - length | mm |  |
| - width | mm |  |
| - height | mm |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Condensate flow: |  |  |
| - nominal | t/h |  |
| - maximum | t/h |  |
| Cooling water flow: |  |  |
| - nominal | t/h |  |
| - maximum | t/h |  |
| Heat transfer surface of the condenser | m2 |  |
| Volume of the water chamber | m3 |  |
| Volume of the steam chamber | m3 |  |
| Useful volume of the collector | m3 |  |
| Vacuum for working point „A“ | kPa |  |
| Vacuum for working point „B“ | kPa |  |
| Condenser pipes: |  |  |
| - length | mm |  |
| - external diameter | mm |  |
| - wall thickness | mm |  |
| - number | items |  |
| - material | - |  |
| Nominal thermal output | MWt |  |
| Temperature difference of emission steam in the condenser and heated cooling water at its nominal output | °C |  |
| Maximum thermal output | MWt |  |
| Total dry weight of the condenser | kg |  |
| Total service weight of the condenser | kg |  |
| System of maintaining vacuum in the condenser (vacuum pumps) |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Vacuum pump type | - |  |
| Amount of exhausted air | kg/s |  |
| Total required amount of cooling water | m3/h |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Number of vacuum pumps | items |  |
| Total weight / unit | kg |  |
| System of continuous cleaning of the condenser pipes |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Number of catch screens | items |  |
| Catch screen diameter | mm |  |
| Amount of recirculating water | kg/s |  |
| Minimum flow rate of cooling water | m/s |  |
| Recirculation pump power input | kW |  |
| Total weight | kg |  |
| Pumps pumping condensate from the condenser (KČKO) |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | items |  |
| Pump type | - |  |
| Number of pumps | items |  |
| Condensate: |  |  |
| - operating temperature | °C |  |
| - maximum operating temperature | °C |  |
| Flow rate: |  |  |
| - maximum | m3/h |  |
| - nominal | m3/h |  |
| - minimum | m3/h |  |
| Nominal delivery head | m of water column |  |
| Minimum suction head | kPa |  |
| Speed: |  |  |
| - nominal | rpm |  |
| - minimum | rpm |  |
| Efficiency for operating point | % |  |
| Nominal power input of the pump | kW |  |
| Material: |  |  |
| - casing | - |  |
| - impeller | - |  |
| Pump output control method | - |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Electromotor: |  |  |
| - manufacturer | - |  |
| - type | - |  |
| - degree of protection | IP |  |
| - nominal speed | rpm |  |
| - nominal output | kW |  |
| - nominal voltage | V |  |
| - variant | - |  |
| - degree of protection | IP |  |
| Weight of the set | kg |  |
| Low pressure and medium pressure regeneration (to be filled in) for each heater |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Type | - |  |
| Heat transfer surface – LPH (MPH) | m2 |  |
| Heat transfer surface - subcooler | m2 |  |
| Pipes: |  |  |
| - length | mm |  |
| - external diameter | mm |  |
| - wall thickness | mm |  |
| - number | items |  |
| - material | - |  |
| Steam chamber: |  |  |
| - nominal pressure | kPa |  |
| - maximum pressure | kPa |  |
| - maximum temperature | °C |  |
| Condensate: |  |  |
| - maximum amount | t.h-1 |  |
| - pressure loss at maximum flow rate | kPa |  |
| - number of ways of the condensate | items |  |
| Heat output of the heater including subcooler | kW |  |
| Difference of end temperatures | °C |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Total weight | kg |  |
| Internal cooling circuit |  |  |
| Plate heat exchanger |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Number of pieces | items |  |
| Cooling water flow (closed system) | l/s |  |
| Cooling water inlet temperature | °C |  |
| Cooling water outlet temperature | °C |  |
| Cooled water inlet temperature | °C |  |
| Cooled water outlet temperature | °C |  |
| Power output | kW |  |
| Pressure loss Δp | kPa |  |
| Heat transfer surface | m2 |  |
| Nominal inside diameter for cooling water connection | mm |  |
| Nominal inside diameter for cooled water connection | mm |  |
| Total weight | kg |  |
| Circulation pumps of the internal cooling circuit |  |  |
| Manufacturer | - |  |
| Pump type | - |  |
| Number of pumps | items |  |
| Cooling water: |  |  |
| - operating temperature | °C |  |
| - maximum operating temperature | °C |  |
| Flow rate: |  |  |
| - maximum | m3/h |  |
| - nominal | m3/h |  |
| - minimum | m3/h |  |
| Nominal delivery head | m of water column |  |
| Minimum suction head | kPa |  |
| Speed: |  |  |
| - nominal | rpm |  |
| - minimum | rpm |  |
| Efficiency for operating point | % |  |
| Nominal power input of the pump | kW |  |
| Material: |  |  |
| - casing | - |  |
| - impeller | - |  |
| Pump output control method | - |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Electromotor: |  |  |
| - manufacturer | - |  |
| - type | - |  |
| - degree of protection | IP |  |
| - nominal speed | rpm |  |
| - nominal output | kW |  |
| - nominal voltage | V |  |
| - variant | - |  |
| - degree of protection | IP |  |
| Weight of the set | kg |  |

## Heat leading out  – PS - 04

| Heat leading out – PS - 04 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Exchanger - heater of heating water |  |  |  |  |
| Parameter |  | Unit |  | Value / data/ information |
| Heating water flow, min. |  | l/s |  |  |
| Heating water flow, max. |  | l/s |  |  |
| Heating water inlet temperature |  | °C |  |  |
| Heating water outlet temperature |  | °C |  |  |
| Nominal inside diameter of heating water piping |  | DN: |  |  |
| Nominal pressure of heating water |  | PN |  |  |
| Inlet steam temperature |  | °C |  |  |
| Condensate outlet temperature |  | °C |  |  |
| Power output |  | MW |  |  |
| Pressure loss Δp |  | kPa |  |  |
| Heat transfer surface |  | m2 |  |  |
| Total weight |  | kg |  |  |
| Manufacturer |  | - |  |  |
| Condensate pumps of condensate from heating water heater (KČOTV) |  |  |  |  |
| Parameter |  | Unit |  | Value / data/ information |
| Manufacturer |  | - |  |  |
| Type |  | items |  |  |
| Pump type |  | - |  |  |
| Number of pumps |  | items |  |  |
| Condensate: |  |  |  |  |
| - operating temperature |  | °C |  |  |
| - maximum operating temperature |  | °C |  |  |
| Flow rate: |  |  |  |  |
| - maximum |  | m3/h |  |  |
| - nominal |  | m3/h |  |  |
| - minimum |  | m3/h |  |  |
| Nominal delivery head |  | m of water column |  |  |
| Minimum suction head |  | kPa |  |  |
| Speed: |  |  |  |  |
| - nominal |  | rpm |  |  |
| - minimum |  | rpm |  |  |
| Efficiency for operating point |  | % |  |  |
| Nominal power input of the pump |  | kW |  |  |
| Material: |  |  |  |  |
| - casing |  | - |  |  |
| - impeller |  | - |  |  |
| Pump output control method |  | - |  |  |
| Connecting flanges |  |  |  |  |
| - nominal pressure |  | PN |  |  |
| - nominal inside diameter |  | DN: |  |  |
| Electromotor: |  |  |  |  |
| - manufacturer ... |  | - |  |  |
| - type |  | - |  |  |
| - degree of protection |  | IP |  |  |
| - nominal speed |  | rpm |  |  |
| - nominal output |  | kW |  |  |
| - nominal voltage |  | V |  |  |
| - variant |  | - |  |  |
| - degree of protection |  | IP |  |  |
| Weight of the set |  | kg |  |  |
| Facility for the recovery of heat from flue gases |  |  |  |  |
| Heat pump: |  |  |  |  |
| - Manufacturer | - |  |  |  |
| - Type | - |  |  |  |
| - Cooling medium | - |  |  |  |
| - Power input | KWe |  |  |  |
| - Power output | kWt |  |  |  |
| - Type and parameters of other energy (for example, steam) | - |  |  |  |
| - Consumption of other energy (not electricity), for example, steam | t/h (kWt) |  |  |  |
| - Operation range | - |  |  |  |
| - Type | items |  |  |  |
| - Weight: | kg |  |  |  |
| - Main dimensions: (b x l x h) | m |  | x x |  |
| Condensing exchanger: |  |  |  |  |
| - Manufacturer | - |  |  |  |
| - Type | - |  |  |  |
| - Power output | kWt |  |  |  |
| - Composition of condensate | - |  |  |  |
| - Exchanger cleaning system | - |  |  |  |
| - Operation range | - |  |  |  |
| - Type | items |  |  |  |
| - Weight: | kg |  |  |  |
| Main dimensions: (b x l x h) | m |  | x x |  |

## Slag and fly ash system - PS11

| Slag and fly ash system - PS11 |  |  |
| --- | --- | --- |
| Flue-dust fly ash |  |  |
| Content of fly ash in raw flue gas | g/Nm3 |  |
| Quantity of fly ash | kg/h |  |
| Temperature of flue-dust fly ash | °C |  |
| Mechanical transport of fly ash |  |  |
| Number of longitudinal conveyors per 1 line | items |  |
| Transported amount per 1 line | kg/h |  |
| Discharge from boiler and electric filter (double flaps) | type |  |
| Type | items |  |
| Drive type | - |  |
| Electric output of drives | kW |  |
| Cross conveyors |  |  |
| Type | items |  |
| Type | - |  |
| Throughput | t/h |  |
| Power input | kW |  |
| Shredder |  |  |
| Type | items |  |
| Type | - |  |
| Throughput | t/h |  |
| Power input | kW |  |
| Feeding station |  |  |
| Throughput | kg/h |  |
| Volume of interim storage tank | m3 |  |
| Volume of the feeding station reservoir | m3 |  |
| Air consumption for the feeding station | Nm3/h |  |
| Max. operating pressure | MPa |  |
| Material | - |  |
| Electric output of heating | kW |  |
| Switch |  |  |
| Type | items |  |
| Type | - |  |
| Material | - |  |
| Manner of switch control | - |  |
| Pneumatic transport of ash to silo |  |  |
| Pressure air drying | °C |  |
| Operating pressure for fly ash transport | bar |  |
| Number of interim tanks of the feeding station | items |  |
| Number of feeding stations | items |  |
| Number of transport routes | items |  |
| Fly ash silo |  |  |
| Type | items |  |
| Silo volume | m3 |  |
| Gross volume | m3 |  |
| Diameter of the cylindrical part | mm |  |
| Height of the cylindrical part | mm |  |
| Wall thickness | mm |  |
| Total height | mm |  |
| Wall material | - |  |
| Closure at the silo outlet | type |  |
| Releasing device | type |  |
| Discharge element of the silo | type |  |
| Power input of electric heating of the silo | kW |  |
| Insulation type/thickness | mm |  |
| Type of the gauge of level of ash in the silo | - |  |
| Cone |  |  |
| Cone angle | grad |  |
| Height of the conical part | mm |  |
| Discharge method | - |  |
| Manufacturer | - |  |
| Silo filter |  |  |
| Type | items |  |
| Filter type | - |  |
| Manufacturer | - |  |
| Filter efficiency | % |  |
| Filter cleaning method | - |  |
| Dosing of fly ash from the silo |  |  |
| Cell feeder |  |  |
| Manufacturer | - |  |
| Weight | kg |  |
| Material | mat. no. |  |
| Drive type | - |  |
| Weighing vessel |  |  |
| Manufacturer | - |  |
| Vessel volume | m3 |  |
| Weighing method | - |  |
| Screw conveyor |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Dust from the baghouse catalytic filter |  |  |
| Mechanical transport of dust |  |  |
| Number of longitudinal conveyors per 1 line | items |  |
| Transported amount per 1 line | kg/h |  |
| Type | - |  |
| Drive type | - |  |
| Power input | kW |  |
| Cross conveyors |  |  |
| Type | items |  |
| Type | - |  |
| Throughput | t/h |  |
| Power input | kW |  |
| Weight |  |  |
| Type | items |  |
| Type | - |  |
| Throughput | t/h |  |
| Big-bag handling | - |  |
| Washing of fly ash |  |  |
| Operating mode | - |  |
| Method of fly ash discharge | - |  |
| Throughput (converted to dry fly ash) | kg/h |  |
| Wet fly ash throughput | kg/h |  |
| Max. fly ash throughput | kg/h |  |
| Washed fly ash moisture content | % by weight |  |
| Washed fly ash properties (hazardousness) |  |  |
| Mixing equipment |  |  |
| Type | items |  |
| Manufacturer | - |  |
| Type | - |  |
| Material | - |  |
| Transported amount | kg/h |  |
| Power control method | - |  |
| Filter |  |  |
| Type | items |  |
| Manufacturer | - |  |
| Type | - |  |
| Flow rate | l/s |  |
| Hg ion exchanger |  |  |
| Type | items |  |
| Manufacturer | - |  |
| Type | - |  |
| Flow rate | l/s |  |
| Equalizing tank |  |  |
| Type | items |  |
| Max. time of tank filling | h |  |
| Volume | m3 |  |
| Dimensions: Ø x h | m | x |
| Material | mat. no. |  |
| Corrosion protection | - |  |
| Tank weight | t |  |
| Waste water collecting tank |  |  |
| Type | items |  |
| Max. time of tank filling | h |  |
| Volume | m3 |  |
| Dimensions: Ø x h | m |  |
| Wall thickness | mm |  |
| Material | mat. no. |  |
| Corrosion protection | - |  |
| Tank weight | t |  |
| Filling pump of waste water from flue gas scrubber |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Type | items |  |
| Transported amount | m3/h |  |
| Delivery head | m of w.c. |  |
| Pump engine speed | rpm |  |
| Electric input | kW |  |
| Extraction tanks |  |  |
| Type | items |  |
| Suspension dwell time | h |  |
| Volume | m3 |  |
| Dimensions: Ø x H | m | x |
| Wall thickness | mm |  |
| Material | mat. no. |  |
| Corrosion protection internal/external | mm |  |
| Empty tank weight | kg |  |
| Full tank weight | kg |  |
| Mixing equipment |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Type | items |  |
| Speed rate | rpm |  |
| Drive type | - |  |
| Electric input | kW |  |
| Empty tank weight | kg |  |
| Mixing equipment weight | kg |  |
| Tank service weight | kg |  |
| Fly ash dewatering |  |  |
| Operation mode | - |  |
| Manufacturer | - |  |
| Dewatering method | - |  |
| Number of units | items |  |
| Dry content | % |  |
| Net filtration area | m2 |  |
| Transport of washed-out fly ash to the slag bunker |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Number of belt conveyors | items |  |
| Transport capacity | t/h |  |
| Conveyor speed | m/s |  |
| Width | mm |  |
| Length | m |  |
| Belt material | - |  |
| Operation mode | - |  |
| Transport of slag and washed fly ash |  |  |
| Crane |  |  |
| Type | - |  |
| Type | items |  |
| Load bearing capacity | t |  |
| Operation method | - |  |
| Minimum transport capacity | t/h |  |
| Crane rails width | mm |  |
| Crane rails length | mm |  |
| Total height of lift | mm |  |
| Crane span | mm |  |
| Crane travel speed | m/min |  |
| Crane travel engine output | kW |  |
| Crab travel engine output | kW |  |
| Lifting engine output | kW |  |
| Time of switching on the crane travel engine | % |  |
| Time of switching on the lifting engine | % |  |
| Time of switching on the crab engine | % |  |
| Degree of protection of crane engines | IP |  |
| Crab travel speed | m/min |  |
| Crane operator’s booth dimensions | mm | x x |
| Weight of the crane bridge with the drive | t |  |
| Weight of the crab with the drive | t |  |
| Total weight of the crane equipment | t |  |
| Grab | - |  |
| Type | items |  |
| Grab design type | - |  |
| Minimum content of the grab (closed condition) | m3 |  |
| Minimum lifting capacity of the grab (net) | t |  |
| Weight of the grab (empty) | t |  |
| Time for grab closing/opening | s |  |
| Bulk weight of slag | kg/m3 |  |
| Lifting speed | m/min |  |
| Micro-lift speed | m/min |  |
| Belt transport |  |  |
| Inclined belt conveyor of slag and fly ash |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Horizontal conveyor of slag and fly ash |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Cross conveyor of slag and fly ash |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Conveyor manufacturer | - |  |
| Sorting and processing of the mixture of slag and fly ash |  |  |
| Magnetic separator |  |  |
| Type | items |  |
| Type | - |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Induction separator |  |  |
| Type | items |  |
| Type | - |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Sorter |  |  |
| Type | items |  |
| Type | - |  |
| Drum diameter | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Conveyor of 0-16 mm fraction |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Conveyor of 16-32 mm fraction |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |
| Conveyor of oversize particles |  |  |
| Type | - |  |
| Angle | grad |  |
| Belt length | m |  |
| Belt width | mm |  |
| Throughput (min.) | t/h |  |
| Electric input | kW |  |
| Noisiness | dB |  |

## Compressor station and pressure air distribution - PS 12

| Compressor station and pressure air distribution - PS 12 |  |  |
| --- | --- | --- |
| Compressor station |  |  |
| Compressor with integral dryer +3°C | items |  |
| Manufacturer | - |  |
| Compressor type | - |  |
| Dryer type | - |  |
| Working pressure | MPa |  |
| Capacity of one compressor | m3/h |  |
| Capacity control | - |  |
| Efficiency in working point | % |  |
| Primary filtration | - |  |
| Condensate removal | - |  |
| Adsorption dryer -40°C | items |  |
| Air chamber 1 | m3 |  |
| Air chamber 2 | m3 |  |
| Final filtration | - |  |
| Compressor station control, | - |  |
| Visualization | - |  |
| Telemonitoring | - |  |
| Recuperation of heat | - |  |

## Cooling water pumping station – PS 13

| Cooling water pumping station – PS 13 |  |  |
| --- | --- | --- |
| Cooling water circulation pump |  |  |
| Parameter | Unit | Value / data/ information |
| Manufacturer | - |  |
| Pump type | - |  |
| Number of pumps | items | 2 |
| Cooling water: |  |  |
| - operating temperature | °C |  |
| - maximum operating temperature | °C |  |
| Flow rate: |  |  |
| - maximum | m3/h |  |
| - nominal | m3/h |  |
| - minimum | m3/h |  |
| Nominal delivery head | m of water column |  |
| Minimum suction head | kPa |  |
| Speed: |  |  |
| - nominal | rpm |  |
| - minimum | rpm |  |
| Efficiency for operating point | % |  |
| Nominal power input of the pump | kW |  |
| Material: |  |  |
| - casing | - |  |
| - impeller | - |  |
| Pump output control method | - |  |
| Connecting flanges |  |  |
| - nominal pressure | PN |  |
| - nominal inside diameter | DN: |  |
| Electromotor: |  |  |
| - manufacturer | - |  |
| - type | - |  |
| - degree of protection | IP |  |
| - nominal speed | rpm |  |
| - nominal output | kW |  |
| - nominal voltage | V |  |
| - variant | - |  |
| - degree of protection | IP |  |
| Weight of the set | kg |  |
| Dosing of chemicals for external cooling water circuit |  |  |
| Parameter | Unit | Value / data/ information |
| Chemikálie1 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Catch tank capacity | l |  |
| Drive | - |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Chemical 2 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Catch tank capacity | l |  |
| Drive | - |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Chemical 3 |  |  |
| Type | - |  |
| Storage tank capacity | l |  |
| Catch tank capacity | l |  |
| Drive | - |  |
| Pump capacity | l/h |  |
| Outlet pressure | MPa |  |
| Electrical power input | kW |  |
| Regulation | - |  |
| Supply voltage of chemical pumps | V |  |

## Condensate treatment – PS 14

| Condensate treatment – PS 14 |  |  |
| --- | --- | --- |
| To be proposed by the contractor |  |  |

## Waste water treatment - PS 15

| Waste water treatment - PS 15 |  |  |
| --- | --- | --- |
| Specification of treated waste water |  |  |
| Waste water from 1st stage of the scrubber | m3/h |  |
| Waste water from fly ash extraction | m3/h |  |
| Waste water from 2nd stage of the scrubber (SO2) | m3/h |  |
| Drops and washes | m3/h |  |
| Neutralization (lime milk Ca(OH)2) | m3/h |  |
| Hydraulic reserve 30% | m3/h |  |
| Total including reserve | m3/h |  |
| Filter cake | kg/h |  |
| Specification of main components |  |  |
| Waste water cooling | items |  |
| Process tanks | items |  |
| Pumps | items |  |
| Piping systems | - |  |
| Dewatering method | - |  |
| Type (vacuum belt press filter, candle filter, sludge press) | - |  |
| Manufacturer | - |  |
| Waste water collecting tank | m3 |  |
| Waste water pumps | items |  |
| Lime hydrate silo | items |  |
| Lime hydrate silo tank volume | m3 |  |
| Lime hydrate specific consumption | kg/t of waste |  |
| Lime milk preparation | - |  |
| Parameters monitored at the outlet | - |  |
| Consumption of chemicals |  |  |
| Medium 1 (i.e. TMT 15, Na2S) | - |  |
| Storage method | - |  |
| Stock | kg |  |
| Specific consumption | kg/t of waste |  |
| Medium 2 (i.e. FeCl3) | - |  |
| Storage method | - |  |
| Stock | kg |  |
| Specific consumption | kg/t of waste |  |
| Medium 3 (i.e. HCl) | - |  |
| Storage method | - |  |
| Stock | kg |  |
| Specific consumption | kg/t of waste |  |
| Medium 4 | - |  |
| Storage method | - |  |
| Stock | kg |  |
| Specific consumption | kg/t of waste |  |

## Transport equipment - PS 19

| ## Transport equipment - PS 19 |  |  |
| --- | --- | --- |
| Wheel loader |  |  |
| Manufacturer | - |  |
| Type | - |  |
| Max. operating weight | kg |  |
| Total width across wheels | m |  |
| Total length | m |  |
| Max. engine power | kW |  |
| Shovel volume | m3 |  |
| Headroom | m |  |
| Tipping load in full turn | kg |  |
| Working load (50%) | kg |  |
| Tipping height at 45° shovel tilt | mm |  |
| Machine weight | kg |  |
| Service in Czech republic provided by company | - |  |

## Emission monitoring system - PS 22

| Emission monitoring system - PS 22 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Quantities | Unit | Measuring principle | Range | Output signal |
| HCl | mg/Nm3 |  |  |  |
| HF | mg/Nm3 |  |  |  |
| CO | mg/Nm3 |  |  |  |
| SO2 | mg/Nm3 |  |  |  |
| NOX | mg/Nm3 |  |  |  |
| O2 in flue gases | % |  |  |  |
| NH3 | mg/Nm3 |  |  |  |
| TOC | mg/Nm3 |  |  |  |
| TZL | mg/Nm3 |  |  |  |
| Flue gas flow rate | Nm3/h |  |  |  |
| Temperature | °C |  |  |  |
| Pressure | hPa |  |  |  |
| H2O in flue gases | % |  |  |  |
| Measurement | Manufacturer | Instrument/sensor | Calibration | Calibration interval |
| HCl |  |  |  |  |
| HF |  |  |  |  |
| CO |  |  |  |  |
| SO2 |  |  |  |  |
| NOX |  |  |  |  |
| O2 in flue gases |  |  |  |  |
| NH3 |  |  |  |  |
| TOC |  |  |  |  |
| TZL |  |  |  |  |
| Flue gas flow rate |  |  |  |  |
| Temperature |  |  |  |  |
| Pressure |  |  |  |  |
| H2O in flue gases |  |  |  |  |

## Waste water monitoring system – PS 23

| Waste water monitoring system – PS 23 |  |  |
| --- | --- | --- |
| Waste water amount | m3/h |  |
| pH | - |  |
| Temperature | °C |  |
| Turbidity | - |  |
| Conductivity | μS |  |
| Measuring method | - |  |
| Manufacturer | - |  |

## Communication systems - PS 24

| Communication systems - PS 24 |  |  |
| --- | --- | --- |
| Voice and data communication |  |  |
| Data network type | - |  |
| Number of racks | items |  |
| Rack UPS | VAh |  |
| PoE | yes/no |  |
| Equipment supplier | - |  |
| Operation CCTV system |  |  |
| Furnace monitoring | items |  |
| Monitoring of boiler hopper space | items |  |
| Monitoring of shredder hopper space | items |  |
| Monitoring of waste bunker space (thermo) | items |  |
| Level monitoring in the boiler drum | items |  |
| Monitoring of waste in open trucks at the scales | items |  |
| WWTP process monitoring | items |  |
| Entrance area monitoring | items |  |
| Number of monitors | items |  |
| System supplier | - |  |
| Power supply | V |  |
| Backup | - |  |
| Elektrická požární signalizace |  |  |
| Technology | - |  |
| Number of circuits | items |  |
| Number of addressed elements | items |  |
| Number of optoelectronic temperature detectors | items |  |
| Number of break glass push button switches | items |  |
| Number of optical detectors | items |  |
| Number of ionization detectors | items |  |
| Number of sirens | items |  |
| Number of beacons | items |  |
| System supplier | - |  |
| Power supply | V |  |
| Backup | - |  |

## Technical system of physical security - PS 25

| Technical system of physical security - PS 25 |  |  |
| --- | --- | --- |
| Places equipped with cameras | items |  |
| Camera type | - |  |
| Camera manufacturer | - |  |
| Monitors | items |  |
| Monitor manufacturer | - |  |
| Recording device capacity | - |  |
| Recording device manufacturer | - |  |
| Data network type | - |  |
| Structured cabling system | - |  |

## Laboratories – PS 26

| The bidder shall give the list of the supplied laboratory equipment - PS 26 |  |  |
| --- | --- | --- |

# SKŘ

## PS 10	SKŘ - Instrumentation and control system

| Parameter | Unit | Value / data/ information |
| --- | --- | --- |
| DCS |  |  |
| Manufacturer and type of DCS for the automation control level | - / - |  |
| Automation stations: |  |  |
| - Type | - |  |
| - Number of processor automation stations - single/redundant | pc / pc |  |
| - Total number of AI / of which reserve | pc / pc |  |
| - Total number of AO / of which reserve | pc / pc |  |
| - Total number of DI / of which reserve | pc / pc |  |
| - Total number of DO / of which reserve | pc / pc |  |
| Galvanic separation of individual inputs on the AI card | Yes/No |  |
| Input optical members on individual inputs on the DI card | Yes/No |  |
| Time resolution of individual inputs on the DI card | ms |  |
| Time resolution of the sequence of events (including events arising inside the system, such as analogue signal limits, operator’s intervention, etc.) | ms |  |
| DCS software |  |  |
| SW contained in the supply: |  |  |
| - Total number of licences | items |  |
| - SW name, version and location | - / - / - |  |
| - SW name, version and location | - / - / - |  |
| - SW name, version and location | - / - / - |  |
| - SW name, version and location | - / - / - |  |
| PLC automats |  |  |
| Auxiliary PLC automats will be used | Yes/No |  |
| Manufacturer / type / purpose of PLC automat | - / - / - |  |
| Manufacturer / type / purpose of PLC automat | - / - / - |  |
| Manufacturer / type / purpose of PLC automat | - / - / - |  |
| TG control and regulation |  |  |
| Supplier of the hydraulic part of the TG control | - |  |
| Manufacturer of the E-H converters | - |  |
| Electronic part of the TG regulation and protections: |  |  |
| - Manufacturer | - |  |
| - Type | - |  |
| - Output signal selection | 1/2 or 2/3 |  |
| TG overspeed protection | manufacturer / type |  |
| TG Vibrodiagnostics: |  |  |
| - Apparatus manufacturer | - |  |
| - Type | - |  |
| - Total number of sensors | items |  |

# Electrical part

## PS 07   Outlet of electrical power output

| Parameter | Unit | Value / data/ information |
| --- | --- | --- |
| Generator switch: |  |  |
| - Manufacturer | - |  |
| - Type | - |  |
| - Manner of electric arc extinction | - |  |
| - Number of poles | items |  |
| - Class | indoor / outdoor |  |
| - Nominal voltage | V |  |
| - Nominal current | A |  |
| - Nominal voltage of control circuits | V DC |  |
| - Nominal voltage of motor drives | V AC |  |
| Outlet transformer 35/6.3 kV: |  |  |
| - Manufacturer | - |  |
| - Nominal power output | kVA |  |
| - Number of pieces | 1 |  |
| - Type of cooling at output | 70/100% |  |
| - Nominal frequency | Hz |  |
| - Nominal primary voltage and tap voltage | V / % |  |
| - Nominal secondary voltage | V |  |
| - Nominal primary current | A |  |
| - Nominal secondary current | A |  |
| - Connection | - |  |
| - Short-circuit voltage Uk | % |  |
| - No-load losses | kW |  |
| - Short-circuit losses | kW |  |
| - Degree of protection | IP |  |

## PS 08	Own consumption equipment

| Own consumption transformer 6.3/0.4 kV: |  |  |
| --- | --- | --- |
| - Manufacturer | - | DTTO |
| - Nominal power output | kVA |  |
| - Number of pieces | 2 |  |
| - Type of cooling at output | 70/100% |  |
| - Nominal frequency | Hz |  |
| - Nominal primary voltage and tap voltage | V / % |  |
| - Nominal secondary voltage | V |  |
| - Nominal primary current | A |  |
| - Nominal secondary current | A |  |
| - Connection | - |  |
| - Short-circuit voltage Uk | % |  |
| - No-load losses | kW |  |
| - Short-circuit losses | kW |  |
| - Degree of protection | IP |  |
| Tap-changing transformers in case of need: |  |  |
| - Manufacturer | - |  |
| - Nominal power output | kVA |  |
| - Number of pieces | 2 |  |
| - Type of cooling at output | 70/100% |  |
| - Nominal frequency | Hz |  |
| - Nominal primary voltage and tap voltage | V / % |  |
| - Nominal secondary voltage | V |  |
| - Nominal primary current | A |  |
| - Nominal secondary current | A |  |
| - Connection | - |  |
| - Short-circuit voltage Uk | % |  |
| - No-load losses | kW |  |
| - Short-circuit losses | kW |  |
| - Degree of protection | IP |  |
| - Manufacturer of internal equipment (circuit breakers, contactors,…) | - |  |
| Manufacturer of electrical protections of the generator / transformers outlet | - |  |
| DPS 08 Diesel generator: |  |  |
| - Manufacturer | - |  |
| - Nominal power output | kVA |  |
| - Nominal voltage | V AC |  |
| - Diesel generator cooling method | - |  |
| - Time of run per one charge of the tank | h |  |
| - Starting method | electrical/air |  |
| - Max. starting up time | s |  |
| Manufacturer of frequency changers (above 25 kW): | - |  |
| - Manufacturer |  |  |
| - Purpose of use of the frequency changer | list of all applications |  |
| Battery 220 V DC: |  |  |
| - Manufacturer | - |  |
| - Total number | items |  |
| - Total capacity | Ah |  |

# Maintenance of the facility

| Maximum time for replacement of heat transfer surfaces: |  |  |
| --- | --- | --- |
| - Parameter | Unit | Value / data/ information |
| - Inlet evaporator |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Superheater 3 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Superheater 2 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Superheater 1 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Evaporator 3 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Evaporator 2 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Evaporator 1 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Economizer 3 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Economizer 2 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |
| - Economizer 1 |  |  |
| - - whole bundle / first row / last row | hour / hour / hour |  |

# Volume C14 Information on processing of personal data obtained from the data subject and from other sources

- In Volume C14 of the indicative tender / tender the participant shall submit Enclosure 14 – Information on processing of personal data obtained from the data subject and from other sources prepared by the contracting authority and contained in Part 2 of the Procurement Documents.

- In preparing its indicative tender / tender, the participant / contractor shall only fill in the name of the (Participant's) company in paragraphs 1 C), 2 A) and 2 E).

- The participant shall further include in Volume C14 a statement confirming that they accept this Enclosure 14 containing Information on processing of personal data obtained from data subject and from other sources without reservation.

An updated list of sanctioned persons is provided, for example, at the website of Finanční analytický úřad (Financial Analytical Office) here https://www.financnianalytickyurad.cz/povinne-osoby-dle-zakona-c-2532008-sb#rusko-seznam-sankcionovanych-osob