supplement 1

PURCHASER’S Technical  Requirements for the Work

TABLE OF CONTENTS

1.	General project description	11

1.1	Introduction	11

1.2	Construction project information	11

1.3	Construction project management	11

1.3.1	Role of purchaser’s organization	11

1.3.2	Contractor’s management and coordination role	12

1.3.3	Organizational interface and procedures for communication between the purchaser and the contractor	12

1.4	Project location	13

1.4.1	Geographic location	13

1.4.2	Construction site location	13

1.4.3	Infrastructure, utilities and transportation roads	13

1.4.4	Geological, geomorphological and hydrogeological conditions	14

1.4.5	Radon risk	14

1.4.6	Protected zones and areas	14

1.4.7	Location relative to flood zones	14

1.4.8	Seismic conditions	14

1.4.9	Climatic conditions	15

1.4.10	Design limitations resulting from construction site location	16

1.5	Basic information on existing equipment	16

1.5.1	Boiler room KY II	16

1.5.2	Fabric filter	20

1.5.3	Limestone silos	21

1.5.4	Limestone handling system – tank unloading station	22

1.5.5	Agglomeration –  fly ash silo	22

1.5.6	Agglomeration – stabilizate production	23

1.5.7	Dry ash loading station	24

1.6	Basic information on new equipment	24

1.6.1	Purpose of the work	24

1.6.2	Equipment type and configuration	24

1.6.3	Civil part	25

1.6.4	Basic parameters of the work	25

1.7	Work structure	25

1.7.1	Building structures/utility systems	25

1.7.2	Process systems	26

1.8	Materials, media a energies available from the purchaser	28

1.8.1	Limestone	28

1.8.2	Lime (dry hydrate)	30

1.8.3	Fuel for diesel generator – diesel fuel	31

1.8.4	Water	31

1.8.5	Ash	32

1.8.6	Compressed air	33

1.8.7	Electrical energy	34

1.8.8	Heating and return water –tky internal circuit	34

1.9	Links to other projects	34

1.10	Basic information on marking system and equipment coding	35

1.10.1	Position determination – X, Y, Z coordinate system	35

1.10.2	Marking and coding system	35

1.11	Equipment and components used at existing purchaser’s installations	35

2.	Scope of supplies	37

2.1	Subject of the work	37

2.2	Scope of goods deliveries – civil part	39

2.2.1	SO 01 Desulfurization	39

2.2.2	SO 02 limestone suspension preparation	39

2.2.3	SO 03 Electrical substation	40

2.2.4	SO 04 Production and shipment of energo gypsum	40

2.2.5	SO 05 Energo gypsum storage	40

2.2.6	SO 06 Dry ash loading station	40

2.2.7	SO 07 Foundations of steel structures and technological equipment	40

2.2.8	SO 08 Demolition	40

2.2.9	SO 09 Pumping station building	40

2.2.10	SO 10 Elevator structure	41

2.2.11	SO 11 Emergency tank	41

2.2.12	SO 12 Electrical wiring for buildings	41

2.2.13	IO 01 Roads and paved surfaces	41

2.2.14	IO 02 Utilities	41

2.2.15	IO 03 Electrical connection	41

2.2.16	IO 04 External lighting	41

2.3	Scope of goods supply – machine technology, electrical equipment and SKŘ	42

2.3.1	PS 01 lime stone handling	43

2.3.2	PS 02 Flue gas ducts	43

2.3.3	PS 03 Desulfurization	44

2.3.4	PS 04 Operation tanks	45

2.3.5	PS 05  Stabilizate mixing center	46

2.3.6	PS 06  Energo gypsum production	47

2.3.7	PS 07  Dry ash loading	47

2.3.8	PS 08  Pipe bridges, steel structures	47

2.3.9	PS 09  Other pipe distribution systems	47

2.3.10	PS 10  Upgrade  of fabric filters	48

2.3.11	PS 11 High voltage operational distribution system	48

2.3.12	PS 12  EPS	48

2.3.13	PS 13  Low voltage distribution systems	48

2.3.14	PS 14  Instrumentation and control, central control room expansion	49

2.3.15	PS 15  Denitrification (fan and piping systems)	49

2.3.16	PS 16  Lime storage and transportation route	49

2.3.17	PS 17  Raw and saline water route	49

2.4	Spare parts and quick-wear parts	49

2.5	Special tools and instrumentation	50

2.5.1	Special tools	50

2.5.2	Special instrumentation	50

2.6	Supply of services and works	51

2.7	Software user rights	51

3.	Work boundaries	52

4.	Requirements for work technical design	55

4.1	Basic requirements for the entire work	55

4.2	Civil part requirements	56

4.2.1	Applicability of project documents	57

4.2.2	Basic requirements	57

4.2.3	Structural design of buildings	61

4.2.4	Requirements for technical equipment of buildings  – TZB and infrastructure networks	68

4.2.5	Specific requirements for the design of individual building structures	74

4.3	Requirements for machine technology, electrical equipment, SKŘ and related equipment	74

4.3.1	Applicability of project documents	74

4.3.2	Common requirements for equipment of process systems and their subsystems	75

4.3.3	Specific requirement for the design of individual process PSs/DPSs	90

4.3.4	Electrical part	90

4.3.5	SKŘ – instrumentation and control system	104

4.3.6	Emission system monitoring	121

4.3.7	Communication systems	122

5.	Operational requirements	123

5.1	Operational environment	123

5.2	Operation personnel	123

5.3	Operating modes	123

5.3.1	Normal operation	123

5.3.2	Start-up	126

5.3.3	Shutdown	126

5.3.4	Exceptional conditions	126

6.	Maintenance requirements	126

6.1	Basic requirements	126

6.2	Equipment diagnostics	127

6.3	Lighting requirements	127

6.4	Worker safety	128

6.5	Access requirements	128

6.6	Transportation requirements	128

6.7	Special tool supply requirements	129

6.8	Special instrumentation supply requirements	129

7.	Service life requirements	130

8.	Fire protection requirements	131

8.1	General principles for fire safety design	131

9.	Health and safety protection requirements	131

10.	Tests and commissioning	132

10.1	General	132

10.2	Inspections and tests for the acceptance of material and sub-deliveries of mass-produced equipment	133

10.3	Inspections and tests during production of individually manufactured equipment	134

10.4	Inspections and tests of finished products - FAT	134

10.5	Inspections and tests of the civil part	135

10.6	Inspection and tests at acceptance for assembly	136

10.7	Individual tests (IZ) at mechanical completion	136

10.8	Inspections and tests during commissioning	137

10.8.1	Preparation for complex testing	137

10.8.2	Complex test, test "A"	138

10.8.3	Performance test	139

10.9	Test „B“	139

10.9.1	Tests performed by the contractor	139

10.9.2	Guarantee  measurements	139

11.	Documentation provided by contractor	140

12.	Used standards and legal and other regulations	140

12.1	General	140

12.2	Requirement for compliance of the work and its execution with technical standards	140

12.3	Requirements for work implementation compliance with Purchaser´s internal management documentation	141

13.	Construction site information	141

13.1	Construction site preparation and drainage	141

13.2	Conditions for environmental protection during construction, felling of trees	141

13.3	Important overground and underground utilities	142

13.4	Construction site access	142

13.5	Contractor’s working hours	142

13.6	Construction site facilities	142

13.7	Contractor´s activity on the construction site	142

13.8	Water and power connections to construction site facilities	142

13.9	Scaffolding and auxiliary structures	143

13.10	Use of main lifting equipment	144

13.11	Environmental care during construction	144

13.12	Waste management	144

14.	Amendments	145

14.1	Amendment D01 – Zoning permit documentation	145

14.2	Amendment D02 – Dispersion study	145

14.3	Amendment D03 – General layout	145

14.4	Amendment D04 – Technical information on existing fabric filters	145

14.5	Amendment D05 – Electrical part and control systems	145

LIST OF ABBREVIATIONS

| Abbre-viations/ terms | Abbre-viations used in PD-EL | Abbre-viations used in PD-CL | Meaning in English | Meaning in Czech |
| --- | --- | --- | --- | --- |
| A |  |  |  |  |
| ABS | ABS | ABS | Absorber | Absorbér |
| AI | AI | AI | Analog Input | Analogový vstup |
| AO | AO | AO | Analog Output | Analogový výstup |
| ASŘTP | ASŘTP | ASŘTP | Automated technological process control system | Automatizovaný system řízení technologického procesu |
| B |  |  |  |  |
| BAT | BAT | BAT | Best Available Techniques | Nejlepší dostupná technika |
| BO | BO | BO | Ordinary repair | Běžná oprava |
| BOZP | OHS | BOZP | Occupational Health and Safety | Bezpečnost a ochrana zdraví při práci |
| C |  |  |  |  |
| CO | CO | CO | Carbon monoxide | Oxid uhelnatý |
| CO2 | CO2 | CO2 | Carbon dioxide | Oxid uhličitý |
| CPU | CPU | CPU | Central Processing Unit | Procesorová jednotka |
| Č |  |  |  |  |
| ČR | ČR | ČR | Czech Republic | Česká republika |
| ČÚBP | ČÚBP | ČÚBP | Czech Occupational Safety Office | Český úřad bezpečnosti práce |
| ČSN | ČSN | ČSN | Czech technical standard | Česká technická norma |
| D |  |  |  |  |
| DCS | DCS | DCS | Distributed Control System | Distribuovaný řídící systém |
| DN | DN | DN | Diameter Nominal | Jmenovitý průměr |
| DPS | DPS | DPS | Partial process system | Dílčí provozní soubor |
| DSP | DSP | DSP | Building Permit Documentation | Dokumentace pro stavební povolení |
| DUR | DUR | DUR | Construction Location Documentation | Dokumentace pro vydání rozhodnutí o umístění stavby a nebo zařízení |
| E |  |  |  |  |
| EN | EN | EN | European standard | Evropská norma |
| ENGS | ENGS | ENGS | Energo gypsum | Energosádrovec |
| EPS | EPS | EPS | Electrical fire alarm system | Elektrická požární signalizace |
| F |  |  |  |  |
| FAT | FAT | FAT | Factory Acceptance Test | Zkoušky u zhotovitele |
| FM | FM | FM | Frequency convertor | Frekvenční měnič |
| G |  |  |  |  |
| GO | GO | GO | Overhaul | Generální oprava |
| GP | GP | GP | Guaranteed parameters | Garantované parametry |
| GPS | GPS | GPS | Global Positioning System | Systém mobilní navigace |
| H |  |  |  |  |
| Hg | Hg | Hg | Mercury | Rtuť |
| HMI | HMI | HMI | Human Machine Interface | Rozhraní člověk – stroj |
| HUP | HUP | HUP | Main gas shut-off valve | Hlavní uzávěr plynu |
| HVB | HVB | HVB | Main production unit | Hlavní výrobní blok |
| HW | HW | HW | Hardware | Hardware (fyzicky existující technické vybavení) |
| I |  |  |  |  |
| IO | IO | IO | Utility system | Inženýrský objekt |
| ITI | ITI | ITI | Technical Inspection Institute | Institut Technické inspekce |
| IZ | IZ | IZ | Individual tests | Individuální zkoušky |
| K |  |  |  |  |
| KKS | KKS | KKS | Kraftwerk- Kennzeichensystem – Power Plant and Energy Coding System | Kraftwerk- Kennzeichensystem - Elektrárenský a energetický kódovací systém |
| k.ú. | k.ú. | k.ú. | Cadastral area | Katastrální území |
| KY II | KY II | KY II | Komořany Heating plant II | Teplárna Komořany II |
| L |  |  |  |  |
| LF | LF | LF | Fabric filter | Látkový filtr |
| LM | LM | LM | Bedding material | Ložový materiál |
| N |  |  |  |  |
| NB | NB | NB | Connecting point / Terminal point | Napojovací bod / přípojné místo |
| nn | nn | nn | Low Voltage | Nízké napětí |
| NOx | NOx | NOx | Oxides of nitrogen | Oxidy dusíku |
| NTP | NTP | NTP | Network Time Protocol | Protokol pro synchronizaci času v počítačové síti |
| NV | NV | NV | Government Regulation | Nařízení vlády |
| O |  |  |  |  |
| O2 | O2 | O2 | Oxygen | Kyslík |
| OIP | OIP | OIP | Regional Labour Inspectorate | Oblastní inspektorát práce |
| OK | OK | OK | Steel structures | Ocelové konstrukce |
| OS | OS | OS | Operator station | Operátorská stanice |
| P |  |  |  |  |
| PC | PC | PC | Personal computer | Osobní počítač |
| PBŘ | PBŘ | PBŘ | Fire-safety solution | Požárně bezpečností řešení |
| PE | PE | PE | Protective conductor; possibly polyethylene | Ochranný vodič eventuálně polyetylen |
| PKZ | PKZ | PKZ | Inspection and Test Plan | Plán kontrol a zkoušek |
| PLC | PLC | PLC | Programmable Logic Controller | Programovatelný automat pro řízení technologických procesů |
| PM | PM | PM | Terminal point / Connecting point | Přípojné místo / napojovací bod |
| PN | PN | PN | Pressure Nominal | Jmenovitý tlak |
| PO | PO | PO | Fire protection | Požární ochrana |
| PP | PP | PP | Polypropylene | Polypropylen |
| PS | PS | PS | Process system | Provozní soubor |
| PTD | PTD | PTD | Operation and Technical Documentation | Průvodní technická dokumentace |
| PTN | PTN | PTN | Instrumentation voltage transformer | Přístrojový transformátor napětí |
| PTP | PTP | PTP | Instrumentation current transformer | Přístrojový transformátor proudu |
| PVC | PVC | PVC | Polyvinylchloride | Polyvinylchlorid |
| R |  |  |  |  |
| R | R | R | Reference state at 6% O2, 101,325 Pa, 0 °C | Referenční stav při 6% O2, 101,325 Pa, 0 °C |
| Ř |  |  |  |  |
| ŘS | ŘS | ŘS | Control system | Řídící systém |
| S |  |  |  |  |
| SI | SI | SI | International System of Units | Mezinárodní soustava jednotek fyzikálních veličin |
| S-JTSK |  | S-JTSK | System of the Uniform Trigonometric Cadastral Network | Systém jednotné trigonometrické sítě katastrální |
| SKŘ | SKŘ | SKŘ | Instrumentation and Control System | Systém kontroly a řízení |
| SNTP | SNTP | SNTP | Simple Network Time Protocol | Jednoduchý protokol pro synchronizaci času v počítačové síti |
| SO | SO | SO | Building structure | Stavební objekt |
| SO2 | SO2 | SO2 | Sulfur dioxide | Oxid siřičitý |
| SO3 | SO3 | SO3 | Sulfur trioxide | Oxid sírový |
| SW | SW | SW | Software | Software (programové vybavení) |
| T |  |  |  |  |
| TKY | TKY | TKY | Komořany Heating Plant | Teplárna Komořany |
| TP | TP | TP | Technical regulation | Technický předpis |
| TZB | TZB | TZB | Technical equipment of buildings | Technická zařízení budov |
| TZL | TZL | TZL | Total particulate matter | Tuhé znečisťující látky |
| U |  |  |  |  |
| UE | UE | UE | United Energy | United Energy |
| UPS | UPS | UPS | Uninterruptible Power Supply | Nepřerušitelný zdroj energie |
| V |  |  |  |  |
| vn | vn | vn | High Voltage | Vysoké napětí |
| VZT | (HVAC) | VZT | Heating, ventilation and air conditioning | Vzduchotechnika |
| Z |  |  |  |  |
| ZD | ZD | ZD | Tender documentation | Zadávací dokumentace |
| ZS | ZS | ZS | Site facilities | Zařízení staveniště |

# General project description

## Introduction

The construction project named "Environmental Improvement of Source TKY II - Wet Desulfurization" (hereinafter "Desulfurization") includes the construction of wet desulfurization technology for boilers K6 - K10 to ensure compliance with the new emission limits in accordance with the requirements of this CONTRACT and with the conditions laid down in the Air Protection Act No. 201/2012 Coll. and the subsequent Decree No. 415/2012 Coll. of the Ministry of the Environment, which sets emission limits and other conditions for the operation of stationary sources of air pollution.

The construction shall be carried out on UE land adjacent to the main production block.

The implementing of the construction represents an above-limit public procurement contract for construction work, pursuant to Act No. 134/2016 Coll., on public procurement, as amended, and is within the scope and under the conditions described in detail in the CONTRACT and its appendixes subject of the CONTRACTOR’S WORK.

The WORK shall be supplied in the form of turn-key deliveries.

## Construction project information

| Developer/PURCHASER: | United Energy, a.s. |
| --- | --- |
| Registered office at: | Most, Komořany, Teplárenská 2, PSČ 434 01 |
| IČ/ID No: | 273 09 959 |
| DIČ/Tax registration No: | CZ-273 09 959 |
| Construction project name: | Environmental Improvements on Source TKY II - Wet Desulfurization |
| Project characteristics: | New, permanent construction |
| Location of construction: | Czech Republic, Ústí Region, City of Most |
| Cadastral area: | Cadastral area Komořany u Mostu |

## Construction project management

### Role of purchaser’s organization

- The PURCHASER’S organization's role during the construction phase is mainly to:

Ensure investor's obligations with respect to the state administration bodies and provide other support for the project implementation requiring cooperation of third parties (operators or owners of utilities etc.,), including ensuring the implementation of follow-up projects that are not within the scope of WORK.

Assuring conformance with obligations and exercising the rights of the PURCHASER arising from the CONTRACT with the CONTRACTOR.

Coordination of the construction project with follow-up projects and third party activities.

In order to ensure the investor's functions in the preparation and implementation of the project, the PURCHASER has appointed a project team that shall be a partner of the CONTRACTOR’S project team during the implementation of the WORK.

In support of some of the project team's tasks, the PURCHASER uses/shall use the services of selected external engineering and consulting organizations.

Because of the utilization of external organizations for activities related to the WORK, the PURCHASER reserves the right to provide these organizations with the documentation and other information obtained from the CONTRACTOR necessary to monitor the activities of the CONTRACTOR and to support other PURCHASER’S activities, provided that these external organizations shall be bound by the PURCHASER to protect confidential information to the same extent as the PURCHASER is bound itself.

The PURCHASER concurrently reserves the right to provide under the same conditions the relevant documentation and other information obtained from the CONTRACTOR to the contractors selected for the implementation of projects following up the WORK, to the extent necessary for the coordination of the WORK and of these follow-up projects.

All PURCHASER’S relationships to external entities are direct. This means that none of the organizations involved in the preparation and implementation of the construction project is authorized by the PURCHASER to represent its interests vis-à-vis other construction project participants or the state authorities and institutions on its behalf, or to provide any third party with any documentation and information it processes for the PURCHASER or receives in connection with the construction project.

### Contractor’s management and coordination role

Considering that the WORK shall be supplied on turnkey basis, the management of the WORK implementation within the set boundaries of the WORK is the sole responsibility of the CONTRACTOR, including mutual coordination of the CONTRACTOR'S own activities and the activities of all its SUB-CONTRACTORS.

The CONTRACTOR shall furthermore provide to the PURCHASER cooperation and support needed to coordinate the WORK with the other follow-up projects, to achieve compatibility of the WORK and the follow-up projects and to harmonize their design preparation, implementation and commissioning.

These services shall include in particular:

necessary additional information or updating of the WORK documentation necessary for the coordination of the WORK and the follow-up projects;

cooperation in resolving potential conflicts between the WORK and the follow-up projects;

participation of CONTRACTOR’S REPRESENTATIVES at consultations and coordination meetings convened by the PURCHASER.

### Organizational interface and procedures for communication between the purchaser and the contractor

The organizational interface and documentation management procedures, including the rules for mutual communication between the PURCHASER and the CONTRACTOR shall be provided in the Project Administrative Code, to be processed by the CONTRACTOR in accordance with the requirements of the CONTRACT – for details see Chapter. 2.1, Supplement 3 to the CONTRACT.

## Project location

### Geographic location

The WORK shall be implemented in the Ústí nad Labem Region, District of Most, in the cadastral area of Třebušice and Komořany. The area is a part of the town of Most.

### Construction site location

The construction site is located on land plot:

Cadastral area Komořany u Mostu, land plot no. 668893

The land plot is located within the premises of United Energy, a.s.

The location of the CONSTRUCTION SITE is shown in Amendment D01.

### Infrastructure, utilities and transportation roads

The location and layout of all existing infrastructure is shown in Amendment D01 and in the general layout in Amendment D03. The most important utilities passing by or through the future CONSTRUCTION SITE are listed below.

UTILITIES

The following utilities pass through the CONSTRUCTION SITE:

storm water sewer,

sanitary water sewer,

drinking water supply system,

industrial water supply system,

fire water distribution system,

steam pipeline,

hot water pipeline,

medium pressure gas line,

high and low voltage power lines,

computer network, telecommunications, internet (internal WiFi network).

ACCESS FOR TRANSPORTATION

Road Transportation

The CONSTRUCTION SITE is accessible from the local road Teplárenská.

Railroad siding

It is located southwest of the CONSTRUCTION SITE. The siding is connected to the track 130 Ústí nad Labem - Chomutov.

The use of rail transport is possible after consultation with the relevant stakeholders. The  CONTRACTOR has the possibility to use this mode of transportation.

### Geological, geomorphological and hydrogeological conditions

In the area of the future CONSTRUCTION SITE, the following surveys have been carried out:

Mining expert‘s opinion statement from 05/2008, prepared by Ing. Svatopluk Havrlík, under serial number 289 of the expert’s journal.

Engineering geology survey from 05/2008, prepared by RNDr. Peter Horváth

The conclusions from the surveys are provided in Amendment D01, the complete documentation can be requested from the PURCHASER, in Czech language, if required.

### Radon risk

Regarding risk of radon penetrating from the subsoil, the COSNTRUCTION SITE  is located in the medium radon index area.

### Protected zones and areas

The CONSTRUCTION SITE is located outside protected areas of natural water accumulation or their protection zones. The Krušné hory protected area of natural groundwater accumulation is located approximately 6.5 km to the northeast.

There is no specially protected area or its protection zone in the immediate vicinity of the CONSTRUCTION SITE. The nearest protected area according to the Act No. 114/1992 Coll. is the National Nature Reserve Jezerka, situated about 6.5 km to the NW and the Protected Landscape Area of České středohoří, the border of which passes about 10 km southeast of the CONSTRUCTION SITE.

The CONSTRUCTION SITE is located outside of sanitary water protection zones.

The CONSTRUCTION SITE is located outside of historical monument conservation zones and also outside the protection zones.

There are no cultural monuments on the CONSTRUCTION SITE.

The CONSTRUCTION SITE is not located in a mining area and is not, pursuant to the provisions of Section 43, considered to be a protected deposit area under the provisions of the Mining Act.

The CONSTRUCTION SITE is located outside of the forest protection zone (50 m), pursuant to Section14 of Act No. 289/1995 Coll. as amended (The Forest Act, amending and supplementing certain acts).

The CONSTRUCTION SITE neighbors on  the protection zones of these roads and utilities:

Railroad line - protection zone of the railroad line Most - Chomutov and the railroad line of SEVEN, a.s. coal cleaning plant - pursuant to Act No. 266/1994 Coll. - 60 m from the outer track axis, but at least 30 m from the perimeter of the track.

110 kV power line - according to Act No. 458/2000 Coll. - 12 m from the outer conductor.

HVB protection zone - 20 m

### Location relative to flood zones

The  CONSTRUCTION SITE does not require any special measures.

### Seismic conditions

The CONSTRUCTION SITE belongs to areas with very low seismic activity.

The seismic activity in the vicinity of the CONSTRUCTION SITE is according to ČSN EN 1998-1 in a zone with an intensity of less than 6° M.C.S. (modified Mercalli-Cancani-Sieberg scale).

There is no need to consider the effect of earthquakes in this area and there are no special for the equipment supplied.

### Climatic conditions

The CONSTRUCTION SITE is located in the T2 climate zone, which is characterized by a long, warm and dry summer and short, slightly warm and very dry winter. The mesoclimate of the area may be partly influenced by the anthropogenic transformation of the relief. Regarding long-term average, the air temperature value in the Most area (the proximity of Most) is above average. On the contrary, the long-term precipitation total is below the average of the Czech Republic - the area southwest of Most belongs to the driest regions of the Czech Republic due to the Krušné Mountains elevation blocking the precipitation. Due to the prevailing western air flow over Central Europe, winds with western direction component also predominate in the Most area - because of the position in an elongated depression, the southwestern winds are the most common, and e.g. in contrast with the Krušné Mountains, wind direction from east to northeast is also important. The windless period is around the average value for the Krušné Mountains foothills, i.e. about 15%.

Nominal winter temperature	-12 v (windy area)

Characteristic snow weight value	0.7 kN/m2 1 – area according to ČSN EN 1991-1-3 ed.2

Average annual air temperature: 	8 - 9 °C

Number of freezing days in a year: 	100 - 120

Number of summer days in a year: 	40 - 60

Average annual total precipitation: 	450 - 650 mm

Number of days with precipitation of more than 1 mm: 	80 - 90

Number of days with snow cover in a year: 	20 - 50

Maximum snow cover: 	20 - 40 cm

Precipitation total in summer period: 	200 - 300 mm

Precipitation total in winter period: 	250 - 350 mm

Cloud cover, annual: 	60 – 75 %

Sun shine: 	1600 h/year

Dominant wind direction: 	SW, W, NW

Daily extremes (Meteorological station Ústí nad Labem):

| Maximum temperature: | 36.5 °C | August 13,2003 |
| --- | --- | --- |
| Minimum temperature: | -22.1°C | January 9,1985 |
| Precipitation: | 59.7 mm | August 12, 2002 |
| Maximum wind burst: | from direction 280° - 44.1 m.s-1 | January 19, 2007 |

### Design limitations resulting from construction site location

The technical design of the WORK and the way it is implemented must respect all restrictions imposed by the location of the WORK within the premises of the operating UE heating plant, in particular the limitations resulting from:

Layout restrictions arising from the location and configuration of the existing buildings and heating plant premises and existing utilities within the UE area.

Existing configuration of connected technologies (including electrical, CCTV and other low-voltage distribution systems such as fire alarm, telephone lines, camera systems, etc.).

Existing protection zones.

Existing geological, geomorphological, hydrogeological, climatic and seismic conditions at the WORK site.

Existing or planned communications and access routes.

The necessity of implementing the WORK without limiting the operation of the UE heating plant beyond the specified times for connecting the WORK to existing technologies. Therefore, there must be no situations where the operator is forced to shut down equipment or reduce production due to improper activities of the CONTRACTOR.

From safety-related rules arising from applicable standards and regulations, and the relevant governing guidelines of the operator, in particular the Guideline No. SM-UE-1805 "Contractors' Code of Conduct" (see  Supplement 11 of the CONTRACT).

Conditions of the building permit being developed.

Other conditions that exist at the site of the WORK.

More detailed information on the initial and limiting conditions at the place of installation, dimensional, time, capacity, organizational, legislative and technical restrictions are provided further in this Supplement 1 to the CONTRACT and in its Amendment D01.

## Basic information on existing equipment

### Boiler room KY II

The boiler room KY II is fitted with 5 fluid boilers. These are drum boilers with a natural circulation of steam-water mixture in boiler tubes and membrane walls forming the walls of the furnace boosted by circulating pumps in the bottom fluidized bed evaporators.

Boilers KY II have a membrane wall, their nominal steam output is 140 t/h and the overload capacity is 154 t/h, the nominal steam temperature is 490 °C and the pressure is 7.5 MPa.

Boilers KY II have the same stationary bubble fluid furnace; it is a transitory type of a stationary furnace with circulating fluidized bed (cirkofluid).

Flue gas parameters on boiler room output:

Maximum operational boiler room state:

Parameters guaranteed by the PURCHASER:

| Description | Unit | Value |
| --- | --- | --- |
| Q wet flue gas | Nm3/h | 800,000 |
| Moisture content | % | 14.1 |
| O2 wet flue gas | % | 5.15 |
| SO2 | mg/Nm3 R | 4,291 |
| SO2 | kg/h | 2,949 |
| HCl | mg/Nm3 R | 50 |
| HF | mg/Nm3 R | 25 |
| TZL before fabric filter | g/Nm3 R | 139 |
| Flue gas temperature before fabric filter | °C | 135 |

Indicative parameters:

| Popis | Jednotka | Hodnota |
| --- | --- | --- |
| O2 dry flue gas | % | 6 |
| NOx | mg/Nm3 R | 180 |
| SO3 | mg/Nm3 R | 200 |
| Hg | mg/Nm3 R | 0.0070 |
| Average ash production (fabric filter + bedding material) | t/h | 52.01 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -1.12 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.26 |
| Q dry flue gas (6% O2, 101,325 Pa, 0°C) | Nm3/h R | 687,415 |

Operational state boiler room 1:

Parameters guaranteed by the PURCHASER:

| Description | Unit | Value |
| --- | --- | --- |
| Q wet flue gas | Nm3/h | 593,416 |
| Moisture content | % | 14.4 |
| O2 wet flue gas | % | 3.85 |
| SO2 | mg/Nm3 R | 3,206 |
| SO2 | kg/h | 1,792 |
| HCl | mg/Nm3 R | 10 |
| HF | mg/Nm3 R | 5 |
| TZL before fabric filter | g/Nm3 R | 139 |
| Flue gas temperature before fabric filter | °C | 136 |

Indicative parameters:

| Description | Unit | Value |
| --- | --- | --- |
| O2 dry flue gas | % | 4.5 |
| NOx | mg/Nm3 R | 180 |
| SO3 | mg/Nm3 R | 120 |
| Hg | mg/Nm3 R | 0.0047 |
| Average ash production (fabric filter + bedding material) | t/h | 30.7 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -0.84 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.26 |
| Q dry flue gas (6% O2, 101,325 Pa, 0°C) | Nm3/h | 558,930 |

Operational state boiler room 2:

Parameters guaranteed by the PURCHASER:

| Description | Unit | Value |
| --- | --- | --- |
| Q wet flue gas | Nm3/h | 421,550 |
| Moisture content | % | 14.0 |
| O2 wet flue gas | % | 4.30 |
| SO2 | mg/Nm3 R | 3,206 |
| SO2 | kg/h | 1,240 |
| HCl | mg/Nm3 R | 10 |
| HF | mg/Nm3 R | 5 |
| TZL before fabric filter | g/Nm3 R | 139 |
| Flue gas temperature before fabric filter | °C | 136 |

Indicative parameters:

| Description | Unit | Value |
| --- | --- | --- |
| O2 dry flue gas | % | 5.0 |
| NOx | mg/Nm3 R | 180 |
| SO3 | mg/Nm3 R | 120 |
| Hg | mg/Nm3 R | 0.0047 |
| Average ash production (fabric filter + bedding material) | t/h | 21.3 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -0.74 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.26 |
| Q dry flue gas (6% O2, 101,325 Pa, 0°C) | Nm3/h | 386,783 |

Operational state boiler room 3:

Parameters guaranteed by the PURCHASER:

| Description | Unit | Value |
| --- | --- | --- |
| Q wet flue gas | Nm3/h | 203,916 |
| Moisture content | % | 13.3 |
| O2 wet flue gas | % | 5.20 |
| SO2 | mg/Nm3 R | 3,206 |
| SO2 | kg/h | 567 |
| HCl | mg/Nm3 R | 10 |
| HF | mg/Nm3 R | 5 |
| TZL before fabric filter | g/Nm3 R | 138 |
| Flue gas temperature before fabric filter | °C | 139 |

Indicative parameters:

| Description | Unit | Value |
| --- | --- | --- |
| O2 dry flue gas | % | 6.0 |
| NOx | mg/Nm3 R | 180 |
| SO3 | mg/Nm3 R | 120 |
| Hg | mg/Nm3 R | 0.0047 |
| Average ash production (fabric filter + bedding material) | t/h | 9.7 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -0.50 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.26 |
| Q dry flue gas (6% O2, 101,325 Pa, 0°C) | Nm3/h | 176,795 |

Operational state boiler room 4:

Parameters guaranteed by the PURCHASER:

| Description | Unit | Value |
| --- | --- | --- |
| Q wet flue gas | Nm3/h | 600,000 |
| Moisture content | % | 14.4 |
| O2 wet flue gas | % | 4.71 |
| SO2 | mg/Nm3 R | 6,801 |
| SO2 | kg/h | 3,610 |
| HCl | mg/Nm3 R | 20 |
| HF | mg/Nm3 R | 40 |
| TZL before fabric filter | g/Nm3 R | 137 |
| Flue gas temperature before fabric filter | °C | 136 |

Indicative parameters:

| Description | Unit | Value |
| --- | --- | --- |
| O2 dry flue gas | % | 5.5 |
| NOx | mg/Nm3 R | 185 |
| SO3 | mg/Nm3 R | 200 |
| Hg | mg/Nm3 R | 0.0047 |
| Average ash production (fabric filter + bedding material) | t/h | 35.6 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -0.84 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.26 |
| Q dry flue gas (6% O2, 101,325 Pa, 0°C) | Nm3/h | 530,157 |

Medium term operating range – parameters guaranteed by the PURCHASER:

| Description | Unit | Min. Value | Max. Value |
| --- | --- | --- | --- |
| Q wet flue gas | Nm3/h | 120,000 | 800,000 |
| Moisture content | % | 12 | 16 |
| O2 dry flue gas | % | 3 | 9 |
| O2 wet flue gas | % | 2.64 | 7.56 |
| SO2 | mg/Nm3 R |  | 10,300 |
| SO2 | kg/h |  | 3,610 |
| HCl | mg/Nm3 R |  | 50 |
| HF | mg/Nm3 R |  | 90 |
| NOx | mg/Nm3 R | 165 | 200 |
| SO3 | mg/Nm3 R | 50 | 200 |
| Hg | mg/Nm3 R |  | 0.0100 |
| TZL before fabric filter | g/Nm3 R |  | 250 |
| Flue gas temperature before fabric filter | °C | 125 | 180 |
| Average ash production (fabric filter + bedding material) | t/h | 6 | 62.9 |
| Fabric filter difference (intake SV – entry to fabric filter) | kPa (g) |  | -2.35 |
| Pressure (+)/Vacuum (-) after KV | kPa (g) | -0.65 | 0.3 |
| Pressure(+)/Vacuum(-) at location of TZL measurement | kPa (g) | -0.6 | 0.25 |
| Vacuum close to transfer point before fabric filter | kPa (g) | -0.30 | -1.40 |

Note: The values in the columns "Min. Value" and "Max. Value" mean the variance of the values of the single parameters regardless of the particular operating mode.

### Fabric filter

Flue gas from the K6-K10 boilers is fed through a fabric filter,  flue gas fan, and flue gas ducts into the stack. The fly ash from the fabric filter is re-injected into the fluidized bed via fly ash intermediate storage or fed as the bedding material from the boiler to the agglomeration silos.

Two four-chamber fabric filters with 4 bypass plate valves (4 pcs), type 2x (4)RP-18-225-D6 are installed on each boiler.

Hose cleaning (regeneration) is carried out by compressed air with a pressure of 0.6 ÷ 0.8 MPa from the instrument air distribution system (see Chapter 1.8.6.1).

Technical parameters – data provided for 2 filters (8 chambers total):

| Filter type |  | 2x(4)RP-18-225-D6 |  |
| --- | --- | --- | --- |
| Total filter area |  | 4,734 | m2 |
| Number of filter hoses |  | 1,800 | ks |
| Filter weight |  | 166,500 | kg |
| Filter hose | Dimension | D6-18 |  |
|  | Material | materials based on PPS |  |
| Support baskets | Dimension | D6-18/16/AKV |  |
|  | Material | 17 246 |  |
| Venturi tube | Dimension | D6 |  |
|  | Material | 11 321 |  |
| Membrane valves | Type | RCA 45T2 – Buna N |  |
|  | Number | 120 | ks |
| Solenoid valves | Type | RCA 3D2T |  |
|  | Number | 120 | ks |

Performance parameters:

| Flue gas flow | Designed | 172,300 | Nm3/h |
| --- | --- | --- | --- |
| Gas temperature | Operational | 132-160 | °C |
|  | Maximum | 180 | °C |
| Vacuum in filter | Maximum | 5 | kPa |
| Pressure in filter | Maximum | 5 | kPa |
| Input TZL concentration | Maximum | 250 | g/Nm3 |
| Output TZL concentration | Guaranteed | 25 | mg/Nm3 |
| Air pressure | Maximum | 0.8 | MPa |
|  | Minimum | 0.6 | MPa |

When reaching 180 °C, the LF is shut down and the flue gas passes through the so-called By Pass (T> 180 °C). At this time, the higher flue gas temperature with a maximum of 200 °C is reached.

Additional information is provided in Amendment D04.

### Limestone silos

The limestone silo (ZS) is a cylindrical vessel made from sheet steel with a designed thickness of 10 mm with a slightly conical metal sheet bottom with a designed thickness of 12 mm and an even flat ceiling. The silos are built on 8 supporting pillars anchored in a concrete foundation blocks. The body of the silo is reinforced on the outer surface by steel sections.

Inside, at the level of +9.5 m, a sedimentation chamber is installed to pre-capture dust from the conveying air. In the center of the bottom of the silo is a discharge hole above which a metal sheet cone is installed to protect the discharge hole against limestone impact and congestion of the outlet opening into the transport container. At the bottom of the silo there is also aeration in the form of aerating troughs. At the outlet of the silo, sampling points for taking limestone samples are installed.

On the silo ceiling 2 safety valves are installed, set at pressure of 30 kPa and vacuum of 30 kPa, bottom entry hatch, dust removal equipment, level measuring probe, 2 limestone inputs into silos and 1 vacuum inlet for the transport container under the limestone silo. Silos No. 1 - 2, 3 - 4 are connected by a duct for duplicate dust removal.

The total number of silos in limestone management is 4. Two limestone unloading stations are installed for each silo - for details, see Chapter Tank unloading station.

Technical parameters:

| Parameter | Unit | Value |
| --- | --- | --- |
| Effective capacity | t | 1,260 |
| Effective volume | m3 | 900 |
| Total volume | m3 | 1,000 |
| Internal diameter | m | 9 |
| Cylinder height | m | 16 |
| Total height without dust removal equipment | m | 21 |
| Maximum pressure | Pa | 25,000,000 |

### Limestone handling system – tank unloading station

Each silo has 2 tank unloading stations located on its sides. Each station consists of:

filling pipe line with DN100 terminal with a manual shut-off valve (each filling line feeds only the respective silo)

compressed conveying air duct fitted with a pressure regulator with DN80 terminal with a manual and pneumatic shut-off valve.

Tank and silo interconnection is carried out using reinforced hoses - limestone unloading hoses and air hoses for driving the compressed air. After the connection, air is fed into the tank by the air hose, which pushes the limestone from the tank through the unloading hose and the filling line into the silo.

The emptying of the tanks is controlled by the limestone system operator. The hose connection, including the conveying compressed air hose, is carried out by the tank truck driver.

### Agglomeration –  fly ash silo

Two fly ash silos are a part of the agglomeration technology. The agglomeration silo is a cylindrical vessel mounted in a special steel structure. The lower bottom of the silo is at a height of 26 m, the top lid at a height of 40 m.

The lower bottom of the silo with installed aeration troughs slopes slightly to the center. A protective metal sheet cone is installed above the drain hole. The lower part of the silo is thermally insulated.

On the upper lid of the silo, outside the ash inlet cabinets, the outlets of ducts venting the inner protective cone and the stabilizate mixer are installed.

Technical parameters:

| Parameter | Unit | Value |
| --- | --- | --- |
| Number | pcs | 2 |
| Silo diameter | m | 9 |
| Silo height | m | 14 |
| Total volume | m3 | 900 |
| Effective volume | m3 | 750 |

### Agglomeration – stabilizate production

The production of stabilizate takes place in a device called a mixer. The mixer is a cylindrical vessel in which blades are installed on a shaft for mixing and discharging the stabilizate. The mixer is continuously mixing the ash with water to the initial reaction to produce the stabilizate.

Technical parameters:

| Parameter | Unit | Value |
| --- | --- | --- |
| Type | - | HTK 6100 |
| Volume | l | 6,620 |
| Output | m3/hr | 85 – 230 |
| Engine rating | kW | 250 |
| Voltage | kV | 6 |
| Nominal current | A | 31.6 |
| Hydrodynamic coupling - type | - | H2 SH 10A |
| - revolutions | min-1 | 1,445/81.44 |
| - oil volume | l | 45 |

The fly ash for mixer is removed from the agglomeration silo by a drain hole in the center of the bottom of the silo. A manual closing flap is installed here, and under it a pneumatic flap controlled automatically during the operation of the mixer. Behind the pneumatic flap, the ash passes through the control valve through the fluidized trough into a Schenk balance and is passed to the mixer after flow rate measurement. The dry ash flow rate of ranges from 40 to 150 tons per hour and maximum up to 200 tons per hour.

Ash delivery set-up is as follows:

from silo No. 1 to mixer No. 1,

from silo No. 1 to mixer No. 3,

from silo No. 2 to mixer No. 2,

from silo No. 2 to mixer No. 3.

The main source of water for wetting the stabilizate in mixers is the technology process "Delivering saline waste water to ash agglomeration". The technology consists of a saline water accumulation sump  consisting of seven interconnected chambers with a usable capacity of 220 m3.

Saline water from different technologies and raw water is supplied to the accumulation sump.

A pump station with Grundfos pumps is installed at the outlet of the accumulation sump. Water conductivity is measured at the pumping station intake, which is the outlet from the accumulation sump. The pumping station delivers mixing water from the saline accumulation sump to the ash agglomeration process by a delivery pipeline which is connected upstream of the closing fittings into the pump delivery pipes for backup water supply.

The pumping station has the capacity to supply two lines of ash agglomeration at the same time. The required water pressure for ash agglomeration is about 0.5 to 0.7 MPa. The maximum volume flow rate of the pumping station is 200 to 300 m3/hr. The total water demand to ensure the functionality of the ash agglomeration is about 600 to 1020 m3 per day.

Each mixer is supplied separately via an output manual valve, a regulating pneumatic valve, and has a sensor for water flow into the mixer. After the mixer is started, the water dosing to achieve the desired moisture content is performed automatically, depending on the ash flow rate. Three moisture content readings are displayed on the control panel. The operator can regulate it within ± 5% of the specified moisture content, based on own quality assessment of the stabilizate produced.

Wetting is performed automatically to an average moisture content of 36.7% with respect to the current quality parameters of fly ash in the silos.

The main volume of stabilizate transport from the site is carried out by an external road transportation company. The agglomeration is operated in a campaign-like manner. The production and shipment of stabilizate is in most cases performed once a day. The mixing center is usually started up during the morning shift and is operated until a new safe stored volume is reached in agglomeration silos for the following operating period. In the event of an increased production (higher production of dry ash), the agglomeration operating time is also proportionally increased. The output of the agglomeration (production of stabilizate) is maintained at the upper level of one single mixer. In the course of production, the production mixers are swapped to empty both agglomeration silos, or the production is maintained by mixer no. 3. One work shift in a working week is dedicated for routine maintenance of the technology. Outside of the heating season, the weekend operation (Saturday + Sunday) usually takes place only during the Saturday morning shift.

### Dry ash loading station

The dry ash loading station technology (NSSP) serves for the collection and subsequent shipment of dry ash transported by pipeline from KYII boilers. Part of the NSSP is the hopper silo for accumulating fly ash from pneumatic transport and for short-term storage before its loading into tank trucks.

Dry ash loading from silos to tanks is performed by a filling nozzle which is firmly attached to the inlet flange of the tank prior to filling. The nozzle is designed so that the ash cannot be released onto the ground after lifting the nozzle from the tank neck.

## Basic information on new equipment

### Purpose of the work

The purpose of the WORK is to build a wet desulfurization technology for boilers K6 - K10 to ensure the fulfillment of new emission limits in accordance with the requirements of this CONTRACT and pursuant to the conditions stipulated in the Air Protection Act No. 201/2012 Coll. and the subsequent Decree No. 415/2012 Coll. of the Ministry of Environment, which sets emission limits and other conditions for the operation of stationary sources of air pollution. The design emission limits for TZL ≤ 7 mg/Nm3 and SO2 ≤ 100 mg/Nm3 reflect the conclusions of the Best Available Techniques (BAT) Reference Document for Large Combustion Plants; Industrial Emissions Directive 2010/75/EU, as amended. The design emission limit values of SO2≤ 100 mg/Nm3 are in the so-called BAT+ range of the above mentioned document.

### Equipment type and configuration

Desulfurization method - wet flue gas desulfurization taking place in the newly installed absorber. The desulfurized flue gas will go directly into the new stack installed on the absorber.

The desulfurization equipment is to be used in an outdoor configuration, circulation pumps, suspension pumps, water pumps, limestone (lime) thinning tank in an indoor configuration.

The equipment shall be connected to the existing flue ducts of boilers K6 - K10 in order to allow boilers without desulfurization to operate during their start-up or in the event of desulfurization failure. The connection shall be carried out with the plant in operation, the operation of boilers K4 and K5 is presumed.

The following products shall be produced in desulfurization:

- stabilizate made by mixing ash, lime, gypsum suspension and water;

- energo gypsum;

- fly ash.

Products listed under items a) and b) shall certified by the PURCHASER. More detailed information on the products  is provided in Chapter 5.3.1.

### Civil part

The WORK shall include the provision of all necessary building structures. The building structures shall include the full range of construction deliveries and WORKS within the WORK boundaries, including the preparation and modification of the construction site, land utilities and their connection to the existing ones, all necessary changes to existing building structures, etc.

The construction design shall be a combination of reinforced concrete and steel structures, the foundation of which shall corresponds to the nature of the load and the local geological conditions. Ceramic and silicate materials, including lightweight metal/plastic materials, shall be used for the outer skin. Vertical dividing and infill structures shall be made of traditional masonry materials, assembled from silicate or gypsum components.

### Basic parameters of the work

The WORK shall comply with the parameters and conditions set out in Supplement 2 to the CONTRACT, including the manner and conditions for demonstrating these parameters. Penalties for non-compliance with the guaranteed parameters are set out in paragraph 42.2. of the CONTRACT. Other parameters shall be demonstrated by the CONTRACTOR in accordance with the Inspection and test plans and Test programs approved by the PURCHASER - see also Chapter 10 of this Supplement 1 to the CONTRACT– TESTS, TRIALS AND COMMISSIONING and Supplement 3 to the CONTRACT - Documentation.

## Work structure

### Building structures/utility systems

The civil part of the WORK shall be divided into building structures (SOs).

The SOs are further divided into SOs with a character of a structural building (Structural SOs) and SOs with the character of an utility construction (IOs - Utility systems).

Additionally, the structural SOs also include, in addition to the structure itself, their internal installations, elevators and connections to external utilities.

The IOs include technical infrastructure connections to public networks, or to UE networks and internal site engineering networks providing media transport amongst the individual structures.

They also include paved and handling surfaces providing horizontal, or potentially vertical, transportation and handling of materials and raw materials.

The WORK scope includes the following SOs/IOs:

Building structures:

| SO/IO Number | Name |
| --- | --- |
| Building structures |  |
| SO 01 | Desulfurization |
| SO 02 | Limestone suspension preparation |
| SO 03 | Electrical substation |
| SO 04 | Production and shipment of energo gypsum |
| SO 05 | Energo gypsum storage |
| SO 06 | Dry ash loading station |
| SO 07 | Foundations of steel structures and technological equipment |
| SO 08 | Demolition of part of ZV OSE building |
| SO 09 | Pumping station building |
| SO 10 | Elevator building |
| SO 11 | Emergency tank |
| SO 12 | Electrical wiring for building |
| Utility systems: |  |
| IO 01 | Roads and paved surfaces |
| IO 02 | Utilities |
| IO 03 | Electrical connections |
| IO 04 | External lighting |

### Process systems

The process technology part of the WORK shall be divided into Process systems (PS) and their sub-systems (DPS).

The WORK scope includes the following PSs and DPSs:

| PS Number | Name |
| --- | --- |
| PS 01 | Limestone handling |
| DPS 01.1 | Ground limestone (storage, transportation, dosing) |
| DPS 01.2 | Limestone suspension (preparation, transportations to ABS, pipes) |
| PS 02 | Flue gas ducts |
| DPS 02.1 | Flue gas ducts |
| DPS 02.2 | Flue gas duct flaps |
| DPS 02.3 | Booster fan |
| DPS 02.4 | Wet stack |
| PS 03 | Desulfurization |
| DPS 03.1 | Absorber, tank, droplet separator |
| DPS 03.2 | Suspension circulation |
| DPS 03.3 | Tank mixing |
| DPS 03.4 | Oxidation air |
| DPS 03.5 | Ancillary equipment, backup source |
| PS 04 | Operation tanks |
| DPS 04.1 | Gypsum suspension tank 15% |
| DPS 04.2 | Gypsum suspension tank 55%, hydrocyclone |
| DPS 04.3 | Water accumulation tank |
| DPS 04.4 | Absorber emptying circuit |
| DPS 04.5 | Process water circuit (rinsing and cooling) |
| DPS 04.6 | Operation tank emptying circuit |
| DPS 04.7 | Technological accessories |
| PS 05 | Stabilizate mixing center |
| DPS 05.1 | Pneumatic transportation (ash, lime) |
| DPS 05.2 | Pipeline systems (gypsum suspension, water) |
| DPS 05.3 | Stabilizate mixing and shipment |
| DPS 05.4 | Technological accessories |
| PS 06 | Energo gypsum production |
| DPS 06.1 | Vacuum filter, vacuum station |
| DPS 06.2 | Energo gypsum loading equipment |
| DPS 06.3 | Energo gypsum shipment |
| DPS 06.4 | Other accessories (mixers, pumps, conveyors) |
| PS 07 | Dry ash loading |
| DPS 07.1 | Dry ash route to fly ash silos |
| DPS 07.2 | Fly ash shipment silos |
| PS 08 | Pipe bridges, technological OK |
| PS 09 | Other pipe distribution systems |
| PS 10 | Upgrade of fabric filters |
| PS 11 | High voltage operational distribution system |
| PS 12 | EPS |
| PS 13 | Low voltage distribution systems |
| PS 14 | Measuring and control, central control room expansion |
| PS 15 | Denitrification (fan and piping systems) – not part of the WORK |
| PS 16 | Lime storage and transportation route |
| PS 17 | Raw and saline water route |

The CONTRACTOR may propose, where appropriate, additional division of PSs into sub-parts (DPSs) or modify the proposed structure of the WORK into SO, IO and PS, provided that the proposed modifications are submitted to the PURCHASER for approval before using the modified structure.

## Materials, media a energies available from the purchaser

### Limestone

Type 1 (Lime kiln Čertovy schody)

Parameters guaranteed by the PURCHASER:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 | % mass | ≥ | 96 | = | 98.36 |  | Dry |
| MgCO3 | % mass | ≤ | 1.5 |  |  |  | Dry |
| SiO2 | % mass | ≤ | 1 | = |  |  | Dry |
| Al2O3 | % mass | ≤ | 0.2 | = |  |  | Dry |
| Fe2O3 | % mass | ≤ | 0.2 | = |  |  | Dry |
| Moisture | % mass | ≤ | 0.15 |  |  |  | Raw |
| Sieve residue 0.045mm | % mass | ≥ | 12 |  |  |  | Raw |
|  | % mass | ≤ | 20 |  |  |  | Raw |

Indicative parameters:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 | % mass | ≥ |  | = | 98.36 | 98.8 - 99.2 | Dry |
| MgCO3 | % mass | ≤ |  |  |  | 0.65 - 0.95 | Dry |
| SiO2 | % mass | ≤ |  | = | 0.25 | 0.03 - 0.2 | Dry |
| Al2O3 | % mass | ≤ |  | = | 0.03 | 0.03-0.1 | Dry |
| Fe2O3 | % mass | ≤ |  | = | 0.08 | 0.035-0.09 | Dry |
| Sieve residue 0.045mm | % mass | ≥ |  |  |  | 14 - 19 | Raw |
|  | % mass | ≤ |  |  |  |  | Raw |
| Specific surface (Blaine) | cm2/g | ≥ | 3,500 | = | 3,737 |  | according to Blain |
| Reactivity B-U | % CaCO3 |  | 55 | = | 56.05 |  | according to B-U |
| Bulk density - freely settled | kg/m3 |  | 900 |  |  | 940 - 990 | Raw |

Type 2 (Lafarge Cement)

Parameters guaranteed by the PURCHASER:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 | % mass | ≥ | 68.0 | = | 70.5 |  | Dry |
| MgCO3 | % mass | ≤ | 2.5 | = | 1.4 |  | Dry |
| SiO2 | % mass | ≤ | 20.0 | = |  |  | Dry |
| Al2O3 | % mass | ≤ | 6.0 | = |  |  | Dry |
| Fe2O3 | % mass | ≤ | 2.0 | = |  |  | Dry |
| Moisture | % mass | ≤ | 1 |  |  |  | Raw |
| Sieve residue 0.071mm | % mass | ≥ | 25 % | = |  |  | Raw |
|  | % mass | ≤ | 50 % |  |  |  | Raw |
| Sieve residue 0.5 mm | % mass | ≤ | 1 % | = |  |  | Raw |

Indicative parameters:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 | % mass | ≥ |  | = | 70.5 | 70 – 77 | Dry |
| MgCO3 | % mass | ≥ |  | = | 1.4 | 1 – 2 | Dry |
| SiO2 | % mass | ≤ |  | = | 16.8 | 13 – 19 | Dry |
| Al2O3 | % mass | ≤ |  | = | 5.3 | 3.5 – 5.5 | Dry |
| Fe2O3 | % mass | ≤ |  | = | 1.8 | 1.3 – 1.9 | Dry |
| Moisture | % mass | ≤ |  |  | 0.6 | 0.3 – 0.8 | Raw |
| Sieve residue 0.075mm | % mass | ≤ |  | = | 26 |  | Raw |
| Sieve residue 0.09 mm | % mass | ≤ |  | = | 17.4 |  | Raw |
| Sieve residue 0.2 mm | % mass | ≤ |  | = | 1.25 |  | Raw |
| Specific surface (Blaine) | cm2/g | ≥ |  | = | 3,416 |  | according to Blain |
| Reactivity B-U | % CaCO3 |  |  | = | 77 |  | according to B-U (UTZ) |
| Bulk density – freely settled | kg/m3 | ≥ | 700 |  | 890 | 800 – 950 | Raw |

Type 3 (Kotouč Štramberk)

Parameters guaranteed by the PURCHASER:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 + MgCO3 | % mass | ≥ | 96 | = | Not provided |  | Dry |
| MgCO3 | % mass | ≤ | 2 | = |  |  | Dry |
| Moisture | % mass | ≤ | 1 |  |  |  | Raw |
| Sieve residue 0.045 mm | % mass | ≥ | 12 | = |  |  | Raw |
|  | % mass | ≤ | 27 |  |  |  | Raw |

Indicative parameters:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 + MgCO3 | % hm | ≥ |  | = | Not provided | 97.33 | Dry |
| MgCO3 | % hm | ≤ |  | = |  | 1.07 | Dry |
| SiO2 | % mass | ≤ | 2 | = |  | 1.5 | Dry |
| Al2O3 + Fe2O3 | % mass | ≤ | 0.8 | = |  | 0.45 | Dry |
| Fe2O3 | % mass | ≤ | 0.3 | = |  | 0.13 | Dry |
| Moisture | % mass | ≤ |  |  |  | 0.14 | Raw |
| Sieve residue 0.045 mm | % mass | ≥ |  |  |  | 21 | Raw |
|  | % mass | ≤ |  |  |  |  |  |
| Sieve residue 0.063 mm | % mass | ≤ | 15 | = |  | 10.4 | Raw |
|  | % mass | ≥ | 4 | = |  |  |  |

Type 4 (Lime kiln Vitošov)

Parameters guaranteed by the PURCHASER:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CaCO3 + MgCO3 | % mass | ≥ | 98.4 | = | Not provided | Not provided | Dry |
| MgCO3 | % mass | ≤ | 0.7 | = |  |  | Dry |
| Moisture | % mass | ≤ | 1 |  |  |  | Raw |
| Sieve residue 0.071mm | % mass | ≤ | 5.1 |  |  |  | Raw |

Indicative parameters:

| Constituent/ Indicator | Unit |  | Limit Value |  | Measured Value | Usual Range | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SiO2 | % mass | ≤ | 0.9 | = | Not provided | Not provided | Dry |
| Al2O3 | % mass | ≤ | 0.2 | = |  |  | Dry |
| Fe2O3 | % mass | ≤ | 0.2 | = |  |  | Dry |
| SO3 | % mass | ≤ | 0.01 |  |  |  | Dry |
| Sieve residue 0.05mm | % mass | ≤ | 14.7 | = |  |  | Raw |
| Sieve residue 0.09mm | % mass | ≤ | 2.5 | = |  |  | Raw |
| Bulk density – freely settled | kg/m3 | = | 1100 |  |  |  | Raw |

### Lime (dry hydrate)

Lime CL80-Q (R5 Psv) according to EN 459-1:

| Constituent/Indicator | Unit | Value |
| --- | --- | --- |
| CaO + MgO | % | ≥ 80 |
| Sieve residue 0.09 mm | % | < 25 |
| Sieve residue 0.2 mm | % | < 3 |

### Fuel for diesel generator – diesel fuel

The fuel complies with ČSN  EN 590 Automotive Fuels - Diesel - Technical requirements and test methods and complies with standards at fuel stations.

### Water

#### Raw water

Indicative parameters:

| Constituent/Indicator | Unit | Average | Max. Value | Min. Value |
| --- | --- | --- | --- | --- |
| Flow rate/production | t/h | according to connection properties |  |  |
| pH |  | 7.7 | 8.7 | 7.3 |
| K | mS/cm | 401 | 468 | 339 |
| KNK4.5 | mmol/l | 1.12 | 1.41 | 0.86 |
| Tc | mmol/l | 1.09 | 1.22 | 0.95 |
| Ca2+ | mg/l | 26.5 | 32.46 | 17.99 |
| Mg2+ | mg/l | 9.7 | 13.61433 | 0 |
| Alkalinity4.5 | mmol/l | 2.80 | 4.23 | 2.15 |
| Sc(tot.) | mmol/l | 3.68 | 5.56 | 0 |
| Cl- | mg/l | 28.6 | 32.36 | 25.67 |
| SO4-2 | mg/l | 83.4 | 111.68 | 63.4 |
| CODMn | mg/l | 4.64 | 5.8 | 3.2 |
| SS | mg/l | 0.95 | 2.2 | 0.2 |
| SiO2 | mg/l | 9.83 | 13.379 | 4.074 |
| Fe | mg/l | 0.258 | 0.754 | 0.098 |
| Cu | mg/l | 9.86 | 35 | 3 |
| t | °C | 17.1 | 21.7 | 11.6 |

Note: The minimum and maximum flow rate does not reflect the shown combination of minimum and maximum chemical indicators.

#### Saline water

Indicative parameters:

| Constituent/Indicator | Unit | Average | Max. Value | Min. Value |
| --- | --- | --- | --- | --- |
| Flow rate/production | t/day | 334 | 600 | 200 |
| K | mS/m | 101.9 | 320.0 | 21.3 |
| pH |  | 8.6 | 9.4 | 4.9 |
| Cl- | mg/l | 175 | 747 | 2 |
| Alkalinity4.5 | mmol/l | 2.51 | 5.16 | 0.01 |
| CODCr | mg/l | 31.4 | 52.1 | 15.3 |
| Dissolved inorganic salts | mg/l | 685 | 1592 | 220 |

Note: The minimum and maximum flow rate does not reflect the shown combination of minimum and maximum chemical indicators.

#### Fire water

Pressure in firewater piping system is 0.9 MPa.

### Ash

Parameters guaranteed by the PURCHASER:

| Constituent/Indicator | Unit | Max. Value |
| --- | --- | --- |
| Al2O3 | % | 37 |
| SiO2 | % | 60 |
| Fe2O3 | % | 12 |
| CaO | % | 40 |
| Other | % | 39 |

Note:	The composition is provided in the base oxidation form. Other types of compounds are not excluded.

Indicative parameters (two year average):

| Constituent/Indicator | Unit | Min. Value | Max. Value |
| --- | --- | --- | --- |
| MgO | % | 0.90 | 2.25 |
| Al2O3 | % | 2.06 | 31.83 |
| SiO2 | % | 32.07 | 55 |
| P2O5 | % | 0.11 | 0.28 |
| SO3 | % | 1.51 | 7.47 |
| K2O | % | 0.69 | 2.09 |
| CaO | % | 6.57 | 19.22 |
| TiO2 | % | 1.08 | 3.20 |
| MnO | % | 0.03 | 0.10 |
| Fe2O3 | % | 3.83 | 8.28 |

Note:	1. The composition is provided in the base oxidation form. Other types of compounds are not excluded.

2. The composition shown is influenced by the CaO, MgO, SiO2 and Al2O3 content from the dry desulfurization method. A change in composition with higher CaO content will occur especially when operating into the dry stack.

Ash granulometric composition (sieve residue):

Indicative parameters:

| Sieve [mm] | 0.075 | 0.125 | 0.25 | 0.5 | 1 |
| --- | --- | --- | --- | --- | --- |
| LF | 95 – 65% | 40 – 65% | 15 – 30% | up to 5% | up to 1% |
| Sieve [mm] | 0.25 | 0.5 | 1 | 2 | 3 |
| LM | 98 – 95% | 90 – 60% | 65 – 35% | 40 – 15% | 25 – 5% |

The LM ash may contain lumps and agglomerates over 32 mm.

The granulometric composition is impacted by the input from the dry desulphurization method.

Ash production from incineration (LM + LF) averaged in t/h:

| Operating mode | Maximum operating state | Operating state 1 | Operating state 2 | Operating state 3 | Operating state 4 |
| --- | --- | --- | --- | --- | --- |
| Ash production [t/h] | 52.01 | 30.73 | 21.25 | 9.71 | 35.57 |

Anticipated average ash composition without bed desulphurization operation:

Indicative parameters:

| Constituent/Indicator | Unit | Average LM | Average LF |
| --- | --- | --- | --- |
| MgO | % | 0.47 | 0.58 |
| Al2O3 | % | 26.00 | 26.7 |
| SiO2 | % | 53.42 | 52.11 |
| SO3 | % | 0.47 | 0.28 |
| K2O | % | 0.15 | 1.29 |
| CaO | % | 1.69 | 2.25 |
| Fe2O3 | % | 6.51 | 5.58 |
| Other | % | 11.29 | 11.21 |

Anticipated average ash granulometric composition (sieve residue) without bed desulphurization operation:

Indicative parameters:

| Síto [mm] | 32 | 16 | 8 | 4 | 2 | 1 | 0.5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LM | 0% | 2.0% | 4% | 7.7% | 23.3% | 49% | 86.9% |  |
| Síto [mm] | 0.5 | 0.2 | 0.09 | 0.063 | 0.045 | 0.0315 | 0.02 | 0.01 |
| LF | 0% | 2% | 22% | 39.9% | 55.9% | 66.64% | 76.2% | 85.2% |

The LM ash may contain lumps and agglomerates over 32 mm.

### Compressed air

#### Conveying and equipment air supply

| Parameter | Unit | Max. Value | Min. Value |
| --- | --- | --- | --- |
| Operational pressure downstream of compressor | bar (g) | 6 ÷ 6.5 |  |
| Pressure downstream of compressor | bar (g) | 7.8 | 5.5 |
| Cooling temperature /freezing – dew point | °C | -40 | -25 |
| Free capacity | Nm3/h | 500 ÷ 1000 *) |  |
| Production energy demand for GP from UE technology | kWh/Nm3 | 0.115 |  |

*) Higher capacity upon enquiry

#### Conveying air

| Parameter | Unit | Max. Value | Min. Value |
| --- | --- | --- | --- |
| Operational pressure downstream of compressor | bar (g) | 3.5 |  |
| Pressure downstream of compressor | bar (g) | 4.3 | 2.9 |
| Cooling temperature /freezing – dew point | °C | 6 | 3 |
| Free capacity | Nm3/h | 1000 ÷ 5000 *) |  |
| Production energy demand for GP from UE technology | kWh/Nm3 | 0.102 |  |

*) Higher capacity upon enquiry

### Electrical energy

R6KYI, 3PE AC 50Hz 6 kV/IT

R6KYII, 3PE AC 50Hz 6 kV/IT

R6KTI, 3PE AC 50Hz 6 kV/IT

R04KYI, 3PEN AC 50Hz 400/230 V/TN-C

### Heating and return water –tky internal circuit

| Water | Parameter | Unit | Value |
| --- | --- | --- | --- |
| Heating | Temperature | °C | max. 65 |
|  | Pressure | MPa | 0.5 |
| Return | Temperature | °C | according to circuit load |
|  | Pressure | MPa | 0.3-0.4 |

## Links to other projects

WORK connection to other projects supplied by other contractors concurrently or prior to the WORK implementation start are not anticipated.

## Basic information on marking system and equipment coding

### Position determination – X, Y, Z coordinate system

The general map of the UE premises is available in an AutoCad 2002 format.

The coordinate system is S-JTSK and the Bpv altitude system (Baltic after alignment).

### Marking and coding system

To identify the supplied structures, systems and components in WORK documentation as well as their physical marking on labels and stickers at the place of installation, the KKS (Kraftwerk-Kennzeichensystem) identification system shall be applied by the CONTRACTOR.

The system shall be used as a single identification system for all parts of the WORK (buildings, machinery, electrical and SKŘ) and shall allow identification on the basis of the function (Process-Related Identification),  point of installation (Point of Installation Identification) and spatial position (Location Identification).

The method of application of the KKS identification system must be linked to the marking system of the existing equipment and is subject to PURCHASER’S approval.

## Equipment and components used at existing purchaser’s installations

UE uses equipment by the following manufacturers:

| Item | Manufacturer |
| --- | --- |
| Fittings | LDM, KSB |
| Circulation pumps | KSB, Sigma |
| Mixers | MUT, Technix |
| Oxidation blowers | MUT, Technix |
| Re-circulation pumps | Warman, Sigma, KSB |
| Nozzles | Lechler |
| Compressors, blowers | Atlas Copco, Aerzen |
| Fabric filters | Gutsche |
| Engines | SIEMENS, ABB |
| Frequency changer VN | SIEMENS, ABB, Rockwell |
| Frequency changer NN | SIEMENS, ABB, Schneider Electric |
| Transformers VN | BEZ, SGB, ABB, ETRA |
| VN Protection | SIEMENS, ABB |
| NN Protection | Schneider Electric, SIEMENS, ABB |
| Switches | ABB, SIEMENS |
| Cables | KABLO Kladno |
| Steel switchboards | Elektrifikace Železnic, EGEM, Rittal |
| NN Circuit breakers | OEZ Letohrad, Schneider Electric, ABB |
| Temperature sensors | ZPA, JSP |
| Pressure and pressure difference sensors | Emerson, WIKA, Philips, JSP, E&H |
| Flow rate sensors | FISHER-ROSEMOUNT, Level Instrument, Nivelco, E&H, Emerson, Krohne, BHV |
| Water level gauges | Level Instrument, Nivelco, E&H, Emerson, Krohne, BHV |
| Servo drives | ZPA Pečky, Regada, SCHIEBEL, Auma |
| Cables, conductors and accessories | KABLO Kladno |
| Components for termination and connection of conductors | SEZ Dolný Kubín |
| Module housings and switchboards | Rittal |
| Module instruments and accessories | Schneider Electric, OEZ Letohrad, LOVATO, FINDER, |
| Circuit breakers and fuses | OEZ Letohrad |
| Control system | Honeywell - Experion PKS, Siemens |
| Power circuit breakers | OEZ letohrad |
| Industrial switches, sockets and plugs | ABB |
| Instrument and terminal blocks | Elektro VD Bečov nad Teplou, WAGO, OEZ Letohrad, |
| Fuses, fuse bottoms, heads disconnectors and accessories | OEZ Letohrad |
| Storage material | KOPOS Kolín |
| Control lights and control heads | Schneider Electric, Eleco |
| Contactors, relays and transformers | Schneider Electric, FINDER, LOVATO, SIEMENS, SCHRACK, ABB |
| House switches | ABB, Elektro SVIT, Vyrtych, Schneider Electric |
| Measuring instruments, thermometers, clocks | FLUKE, Metra Blansko, Schneider Electric |
| Lighting fixtures | Elektrosvit, Vyrtych |
| Light sources | OSRAM, PHILIPS |
| Steel switchboards | Rittal |

The list provided above is informative and does not imply an obligation of the CONTRACTOR to use these manufacturers.

However, due to the unification and reduction of training and maintenance costs, the above mentioned products are preferred by the PURCHASER for use also within the WORK scope.

# Scope of supplies

## Subject of the work

By signing the CONTRACT, the CONTRACTOR undertakes to execute for the PURCHASER the WORK  “Environmental Improvements on TKY II Heating Plant - Wet Desulfurization” in the form of turnkey delivery in accordance with the requirements, conditions, specifications and other data and information contained in the CONTRACT.

The WORK shall include, and “turnkey” should be taken to mean, in particular the following:

- Assessment and evaluation of existing, and potentially the execution of additional, surveys, documentation, information, and data required to perform the WORK.

- Creation and submission of the DOCUMENTATION FOR EXECUTION OF THE PROJECT such as may be required for the due completion of the WORK in the scope and under the terms specified in the CONTRACT.

- Creation and submission of all other documentation required by Supplement 3 to the CONTRACT.

- Construction of SITE FACILITIES such as may be required to complete the WORK as specified in the CONTRACT and to operate the SITE throughout the WORK, including disposal (particularly, with regard to environmental protection, fire safety, and occupational health and safety as required by applicable legislation).

- Provision, i.e., supply and assembly, of the required publicity tools (project / construction information) pursuant to the Rules for Applicants and Beneficiaries and the Required Publicity Graphics Manual published at http://www.opzp.cz/obecne-pokyny/pravidla-publicity.

- Arrangement of SITE management and transport to and from the SITE, including offloading, toll duty, taxation, insurance, security, and warehousing of all GOODS, materials, components, etc. required to complete the WORK.

- Demolition / disassembly of existing equipment that is to be replaced by newly installed equipment during the WORK, or that becomes redundant through the completion of the WORK.

- Execution of the construction associated with the WORK in the scope and under the terms agreed in the CONTRACT.

- Provision and assembly of the technology associated with the WORK, including machinery and related systems, monitoring and control systems, and electrical technology in the scope and on the terms specified in the CONTRACT.

- Connection of the WORK to existing structures and systems at the connection points defined in Supplement 1 to the CONTRACT.

- Supply of replacement parts in the scope and on the terms agreed in the CONTRACT.

- Supply of any and all special tools and devices required to maintain the WORK once completed in the scope and on the terms agreed in the CONTRACT.

- Overall coordination of all deliveries of GOODS, WORKS, and SERVICES within the scope of the WORK.

- Management, monitoring, execution, inspection, and documentation of the preparation and realization phases of the WORK, including updates and the provision of required organizational and planning documentation in the scope and on the terms agreed in the CONTRACT.

- Maintenance of a Construction Log, execution and / or provision of adequate conditions for the execution of expert oversight pursuant to Czech Ordnance no. 499/2006 on Construction Documentation, as amended (the Construction Log to comply with the requirements given in Czech Ordnance no. 499/2006 on Construction documentation, as amended).

- Achievement and documentation of quality characteristics required by the CONTRACT and pursuant to the QUALITY PLAN, including all applicable inspections and tests in the scope and on the terms agreed in the CONTRACT.

- Achievement and submission of all certificates of quality, materials, material testing, assembly progress, completeness, performed inspections, necessary revision reports, protocols, approvals, attestations, consents, and certificates required to execute, operate / use, and gain official approval for the WORK in the scope and on the terms required by the CONTRACT.

Note: Certification of stabilizate, energo gypsum and fly ash of fabric filter is the responsibility of the PURCHASER, the CONTRACTOR shall provide effective co-operation.

- Provision of RIGHTS OF USE required for use of the WORK, including relevant documentation, in the scope and on the terms agreed in the CONTRACT.

- Removal of all waste materials arising from the realization of the WORK, on the terms required by the CONTRACT.

- Training of the PURCHASER’s operations and maintenance staff, in the scope and on the terms agreed in the CONTRACT.

- Participation of the CONTRACTOR’s responsible staff in the discussion and approval of the documentation prepared pursuant to Supplement 3 to the CONTRACT, during GUARANTEE MEASUREMENT, COMMISSIONING, and the official approval for use process, on the terms required by the CONTRACT.

- COMMISSIONING of the WORK, including all relevant tests and inspections and the completion of the WORK on the terms required by the CONTRACT.

- Provision of adequate conditions for the execution of the GUARANTEE MEASUREMENT by an independent entity, and participation in such tests, including the provision and submission of required documentation.

- Provision of guarantees for the quality of the WORK in the extent specified in the CONTRACT and the removal, free of charge, of any defects that may arise during the WARRANTY PERIOD, under the conditions specified in the CONTRACT.

- Cooperation with and support of the PURCHASER in coordinating the WORK with related projects executed by other providers.

- Cooperation with the Occupational Health and Safety Coordinator and compliance with the suggestions, recommendations, and directives of the same.

The CONTRACTOR shall perform, within the scope of the WORK, all WORKS and SERVICES and deliver all GOODS, including those not explicitly listed in the CONTRACT but that may, logically and in view of the CONTRACT, be reliably deduced to be necessary for the correct functioning and completion of the WORK, this on the same terms as if such WORKS, SERVICES, and GOODS were listed in the CONTRACT.

The subject of the WORK consists of the delivery of GOODS, WORKS, SERVICES, and RIGHTS OF USE, and is further specified in detail in the following sections of this chapter and further described in the other DOCUMENTS of the CONTRACT.

## Scope of goods deliveries – civil part

The supply of GOODS for the civil part of the WORK shall include supplies of GOODS needed for construction work and the complete construction of all building structures and utility systems that are within the scope of the WORK as described in Chapter 1.6.1 of this Supplement 1 to the CONTRACT, including their installation.

These are especially GOODS required for:

Establishing of construction site facilities;

Preliminary work, excavations, foundations, potentially induced relocations of utility networks, outdoor lighting, earthing, etc.;

Construction of complete new structures including their respective installed equipment by building professions (building technology and technical equipment), based on the purpose and needs of the given operation (fire prevention, hygiene, safety and operational requirements). These include, in particular, internal fire water distribution systems, sewerage systems, sanitary equipment, high voltage power lines (including lighting, emergency lighting, wiring for sockets, grounding and conductors), ventilation, air conditioning and heating, including related measurement and control systems. The individual professions shall be provided in sufficient and satisfactory scope be based on the final design of the CONTRACTOR;

Providing buildings with furnishings;

Manufacture of steel, concrete structures, hoist rails, platforms, ladders, staircases;

Building preparation connected with the installation of new machinery equipment, electrical technologies, SKŘ systems and installation of low voltage distribution systems and their anchoring to building structures or as required by power, control and other cable/wire installations;

Roads, walkways, areas, outdoor lighting and grounding.

Detailed information and detailed requirements for the technical design of the civil part of the WORK are provided in Chapter 4.2. and in Amendment D01.

The individual building structures include in particular:

### SO 01 Desulfurization

- This SO includes in particular:

Foundations for the absorber structure connected to the stack;

Individual foundations for equipment within PS 03 - Desulfurization;

Retention sump connected to SO 09 – Pumping station building.

### SO 02 limestone suspension preparation

- This SO includes in particular:

Single-story above-ground structure protecting the process chain for the preparation of the limestone suspension. The below ground segmented sump shall be placed below the level of the foundation plate;

Heating and ventilation of the building using hot-water heating units.

### SO 03 Electrical substation

- This SO includes in particular:

Single-story building for the installing the electrical equipment and measuring and control equipment;

Semi-enclosed cable compartment;

Heating and ventilation of the building using hot-water heating units.

### SO 04 Production and shipment of energo gypsum

- This SO includes in particular:

Three-story steel prefabricated hall housing the pumping station, vacuum stations, energo gypsum silo and shipment facility;

Heating and ventilation of the building using hot-water heating units.

### SO 05 Energo gypsum storage

- This SO includes in particular:

A new part of the retaining wall, adjacent to the existing retaining wall, including drainage;

Concrete paved area (built within IO 01 - Roads and paved areas).

### SO 06 Dry ash loading station

- This SO includes in particular:

Two storage cylindrical magazines on steel structures;

Dry ash shipping facility.

### SO 07 Foundations of steel structures and technological equipment

- This SO includes in particular:

- Concrete foundations and footings for anchoring steel structures and pipeline bridge.

### SO 08 Demolition

- This SO includes in particular:

Demolition of part of the ZV OSE building.

### SO 09 Pumping station building

- This SO includes in particular:

Single-story reinforced concrete hall for pump housing;

Heating and ventilation of the building using hot-water heating units.

### SO 10 Elevator structure

- This SO includes in particular:

A roofed, staircase tower without outer skin;

Enclosed elevator.

### SO 11 Emergency tank

- This SO includes in particular:

Concrete foundation for the emergency tank

### SO 12 Electrical wiring for buildings

- This SO includes in particular:

Lighting wiring (operational and emergency lighting) and socket wiring for all relevant building structures;

Grounding system and network;

Protection against operational and atmospheric overvoltage.

### IO 01 Roads and paved surfaces

- This IO includes in particular:

All roads, paved areas, handling areas within the premises and transportation connections of new structures to existing local area roads;

Delivery and installation of shoulders, kerbs, barriers, traffic signs and other related works and supplies.

### IO 02 Utilities

- This SO includes in particular:

Storm water drainage piping from roofs, staging and driving areas, divided into three main sewers;

Connections from storm water pipes and street inlets.

### IO 03 Electrical connection

- This IO includes in particular:

Related construction works (excavations, bedding fills, fills, backfills, compaction, etc.) related to cable laying.

The outdoor cable wiring is a part of PS 11 High voltage operational distribution system.

### IO 04 External lighting

- This SO includes in particular:

Outdoor lighting of roads and paved areas;

Supply and installation of discharge lamps, their foundation and supporting structures, fitments;

Air traffic warning system for the stack.

## Scope of goods supply – machine technology, electrical equipment and SKŘ

The supplies of GOODS for the WORK process technology shall include the supply of complete technological installations, i.e. the complete supply of equipment, materials, including all overground pipelines connecting existing equipment and all necessary changes to existing equipment, starting with the entry of flue gas, raw materials, auxiliary substances, energies, water etc. and ending at the outlet of the cleaned flue gas from the stack and processing of the desulfurization product.

- The supplies hereinbelow shall be part of the machine technology GOODS supplied within the WORK scope:

Machinery and equipment, including motors.

Pipes, fittings, accessories.

Base frames and anchors of all devices.

Pipeline bridges and steel structures.

Weighing equipment.

Safety covers, insulations and other means to protect against mechanical threat from rotating parts, high temperatures and effects of the processed media.

Safety and protecting equipment of pressure vessels ensuring sufficient depressurization of the container without its destruction in the event of excessive pressure build-up inside the vessel,

Elevators, lifting equipment (cranes, monorail cranes, hoists, etc.) for simple and quick repairs and maintenance of equipment to the required extent.

Distribution of service media (compressed air, water, ...).

Coatings, internal corrosion protection.

Noise damping covers and their accessories.

Devices or elements of measuring and control strings normally provided as part of machinery equipment. These are in particular sampling points for all measurements, built-in sensors or sensors requiring special adaptations of technological equipment such as bearing thermometers, thermometers inside electrical machines, etc., direct display measuring instruments without remote signal transmission. The allocation of these supplies between the process technologies and SKŘ is the responsibility of the CONTRACTOR.

Deliveries of goods necessary for the modification and reconstruction of the existing facility, including adjustments and reconstructions beyond the boundaries of the work where it is necessary to achieve compatibility of the WORK and the existing PURCHASER´S facilities.

The CONTRACTOR may, in logically justified cases, include in the delivery of PS and DPS machinery equipment also some electrical and SKŘ equipment allocated in this Annex 1 to PS 14 – Measurement and control, central control room expansion or PS 11 - Power distribution system. These are the instances where these devices, such as local power switchboard cabinets, autonomous PLCs for process control, etc., are standard equipment of packaged units, or other supplied technological equipment.

In this regard, the CONTRACTOR may, in its supply specification, modify the allocation of supplies among the individual PSs/ DPSs (as opposed to the breakdown provided hereinbelow).

The supply of GOODS for the electrical part of the WORK shall include, in particular, switchboards, transformers and power distribution systems, lighting, SKŘ power supply.

Supply of GOODS for SKŘ shall include, in particular, the new desulfurization control system including complete measuring circuits, instrument supplementation of central control facilities, modification of existing control systems concerned, cabling, grounding, assembly and consumables

Detailed information and detailed requirements for the technical design of the machine technology part, electrical part and the SKŘ part of the WORK are given in Chapter 4 and in Amendment D01.

Supply of GOODS for the individual process systems shall include:

### PS 01 lime stone handling

#### DPS 01.1 Ground limestone

- This DPS includes in particular:

Filling of ground limestone into silos No. 2 and 3;

Storage of ground limestone in silos No. 2 and 3, including possible modifications of silos (filling, aeration, de-dusting);

Transportation and dosing of ground limestone.

#### DPS 01.2 Limestone suspension

- This DPS includes in particular:

Mixing system for the preparation of limestone suspension;

Storage of limestone suspension in an underground tank;

Limestone suspension mixers;

Limestone suspension circulation pumps and dosing into the absorber.

Sound damping;

Lifting equipment for handling and repair.

### PS 02 Flue gas ducts

#### DPS 02.1 Flue gas ducts

- This DPS includes in particular:

Flue gas ducts from the T-piece to the absorber;

Injection device for emergency cooling of flue gas;

Support structures, compensators, flanges, seals, cleaning apertures, etc.

#### DPS 02.2 Flue gas duct flaps

- This DPS includes in particular:

Flaps allowing individual adjustment of the flue gas path for each boiler into the existing dry stack or the new absorber;

Sealing air blowers or use of air from the existing distribution system.

#### DPS 02.3 Booster fan

- This SO includes in particular:

Flue gas booster (ID) fan;

Sound damping;

Power control equipment;

Lifting equipment for handling and repair.

#### DPS 02.4 Wet stack

- This DPS includes in particular:

Wet stack with chemically resistant liner;

Continuous emission measurement according to legislation (within PS 14);

Air traffic warning system on the stack (within IO 04).

### PS 03 Desulfurization

#### DPS 03.1 Absorber, tank, droplet separator

- This DPS includes in particular:

Absorber with counter-current sprinkled flue gas;

Droplet separator installed in upper levels of the absorber.

#### DPS 03.2 Suspension circulation

- This DPS includes in particular:

Circulation pump circuits leading into individual sections of the absorber;

Sound damping;

Lifting equipment for handling and repair.

#### DPS 03.3 Tank mixing

- This DPS includes in particular:

Set of mixers for mixing the circulating limestone suspension;

Lifting equipment for handling and repair.

#### DPS 03.4 Oxidation air

- This DPS includes in particular:

3 circuits of oxidizing air blowers;

Sound damping;

Lifting equipment for handling and repair.

#### Ancillary equipment, backup source

- This DPS includes in particular:

An independent and self-sufficient backup generator (diesel generator) including  fuel tank and control unit must be dimensioned to provide not only a safe shutdown of the equipment but also to keep in operation all process equipment required to prevent subsequent damage due to sedimentation, setting, pollution, etc.;

Sound damping;

Lifting equipment for handling and repair.

### PS 04 Operation tanks

#### DPS 04.1 Gypsum suspension tank 15%

- This DPS includes in particular:

15% gypsum suspension tank as an intermediate tank for energo gypsum production;

Suspension feed pump circuit.

#### Gypsum suspension tank 55%, hydrocyclone

- This DPS includes in particular:

Battery of hydrocyclones used to thicken the gypsum suspension;

Gypsum suspension tank 55%;

Gypsum suspension mixer.

#### DPS 04.3 Water accumulation tank

- This DPS includes in particular:

Water collecting tank;

Water collecting tank mixer;

Water collection pump circuit;

Sound damping;

Lifting equipment for handling and repair.

#### DPS 04.4 Absorber emptying circuit

- This DPS includes in particular:

Emergency tank;

Emergency tank mixers;

Absorber discharge pump and suspension backflow pump circuits;

Sound damping;

Lifting equipment for handling and repair.

#### DPS 04.5 Process water circuit

- This DPS includes in particular:

Rinsing and cooling water tank;

Raw water filters;

Droplet separator pump circuits;

Pump circuits for washing energo gypsum cake on the vacuum filter;

Emergency flue gas cooling pump circuits at the absorber inlet;

Sound damping;

Lifting equipment for handling and repair.

#### DPS 04.6 Operation tank emptying circuit

- This DPS includes in particular:

Underground collection sump;

Collection sump mixer;

Collection sump pump circuits;

Sound damping;

Lifting equipment for handling and repair.

#### DPS 04.7 Technological process accessories

Technological accessories of operation tanks (piping connections, fittings, etc.).

### PS 05 	Stabilizate mixing center

#### DPS 05.1 	Pneumatic transportation (ash, lime)

- This DPS includes in particular:

Pneumatic transport of ash and lime;

The transportation capacity of the lime route is 13 t/h with regard to the mixing center capacity;

If separate air supply will be supplied for the lime pneumatic transport, it is necessary to take into account the waste free nature of the technology or the possible location near the compressor station K5/6 and the capacity of the existing disposal of contaminated condensate.

#### DPS 05.2 	Pipeline systems (gypsum suspension, water)

- This DPS includes in particular:

Pipeline distribution of gypsum suspension and water

#### DPS 05.3 	Stabilizate mixing and shipment

- This DPS includes in particular:

Mixer modification;

Transportation and shipment of stabilizate.

#### DPS 05.4 	Technological process accessories

- This DPS includes in particular:

Gypsum suspension feed pump circuits;

Pipes, fittings.

### PS 06 	Energo gypsum production

#### DPS 06.1 	Vacuum filter, vacuum station

- This DPS includes in particular:

Vacuum filter;

Vacuum pump including air tank;

Filtrate pump circuit.

#### DPS 06.2 	Energo gypsum loading equipment

- This DPS includes in particular:

Energo gypsum conveyor.

#### DPS 06.3 	Energo gypsum shipment

- This DPS includes in particular:

Energo gypsum silo with screw conveyor.

#### DPS 06.4 	Other accessories

- This DPS includes in particular:

Pipe distribution systems.

### PS 07 	Dry ash loading

#### DPS 07.1 	Dry ash route to fly ash silos

- This DPS includes in particular:

Pneumatic transport of dry ash from boilers K6 - K10.

#### DPS 07.2 	Fly ash shipment silos

- This DPS includes in particular:

2 new dry ash silos;

Dry ash loading station;

Relocations and modifications of existing equipment.

### PS 08 	Pipe bridges, steel structures

- This PS includes in particular:

Pipe bridges including steel structures;

Steel structures to support new flue gas ducts.

### PS 09 	Other pipe distribution systems

- This PS includes in particular:

Pipe distribution systems for media transport;

Fittings.

### PS 10 	Upgrade  of fabric filters

- This PS includes in particular:

Fabric filters;

Upgrading of inlet and outlet filter flaps;

Modification of the fly ash removal system (if necessary);

Modifications of the air pressure system for hose cleaning (if necessary).

- Note: When modernizing the fabric filters, the corrosive effect of flue gases untreated by desulfurization must be taken into account.

### PS 11 High voltage operational distribution system

- This PS includes in particular:

- All necessary electrical equipment including cabling to power the newly supplied desulfurization process technology TKY II. The delivery shall include, in particular, the following:

Switchboard 6kV for wet scrubbing power supply;

Modifications to two existing R6KYII substations for wet scrubbing connection;

Modifications to six bays of existing 6kV substations for connecting circulating pumps and 1pc of flue gas booster (ID) fan;

Transformers 6/0.4 kV;

Main and secondary distributors 0.4 kV;

UPS for powering the control system;

Motor wiring installation;

Cabling, including connection to existing switchboards;

Main and complementary interconnections;

Accessories (local control cabinets, switch cabinets, etc.).

### PS 12 	EPS

- This PS shall include in particular:

Automatic EPS fire alarms;

Push-button alarms;

Acoustic and optical alarm signaling devices;

Cabling including connection to existing EPS exchange.

### PS 13 	Low voltage distribution systems

- This PS shall include in particular:

Telephone lines and telephone devices connected to the existing telephone exchange in the existing server room;

Data connection including switches and sockets connected by optical cable to the existing switch in the existing server room.

### PS 14 	Instrumentation and control, central control room expansion

- This PS shall include in particular:

Complete control system equipped with tools for control, protection and monitoring of all desulfurization process technologies;

PLC based autonomous control systems (if their functions are not integrated into the DCS) supplied as equipment component of process equipment (packaged units);

Modification of existing control systems related to the WORK (K6 - K10 boiler control system, pneumatic transportation control system, agglomeration mixing control system, dry ash loading station control system, power supply control system) including signal sharing;

Complete measuring circuits including emission measurements;

Central control room equipment;

Control drives and control valves including all auxiliary devices such as power supplies for control drives, etc.;

Switchboard (cabinets) for transfer relays if used between the control system and the linked systems;

Internal cabling connecting individual components of SKŘ system including marshalling cabinets, if required by the system, including bearing and support structures and fasteners;

External wiring for supplied devices connected to the technological equipment and electrical technology and cable route set-up;

Mounting material for supplied equipment, including cable trays/boxes (if applicable), coating and insulating materials, including the material needed to provide cable routes and fire protection;

Grounding of all equipment supplied;

Consumables and media required for putting the supplied equipment into service for at least one year operation.

### PS 15 	Denitrification (fan and piping systems)

- Note: The process system PS 15 Denitrification is not in the scope of the WORK.

### PS 16 	Lime storage and transportation route

Lime pneumatic transport;

Potential modifications of silo 4 (filling, aeration, dedusting).

### PS 17 	Raw and saline water route

Raw and saline water piping.

## Spare parts and quick-wear parts

Spare parts and quick-wear parts shall be supplied in accordance with Section 35 of the CONTRACT.

## Special tools and instrumentation

### Special tools

The CONTRACTOR shall supply all the special tools required for the repair and maintenance of the WORK, with special tools being tools, devices, and also assembling, transport and other tools specially designed for assembly/dismantling, maintenance, commissioning and testing of the equipment supplied by the CONTRACTOR such as:

Equipment for disassembly and installation of all installed equipment for which it is required for maintenance or repair.

Lifting clamps for dismantling all installed equipment that are required for maintenance or repair.

Special keys for atypical or inaccessible nuts, resp. connecting elements.

Equipment for mounting and dismantling of all installed equipment that is required for maintenance or repair.

Set of tools needed to set up the individual machines.

This equipment shall include, among other things, all assortment of special tools that shall be used by the CONTRACTOR for installation, commissioning, operation and troubleshooting of the WORK. This means that the CONTRACTOR shall not use other kind and types of special tools for these purposes than those concurrently supplied to the PURCHASER.

Special tools shall be delivered in numbers and types corresponding to the usual maintenance method.

Standard, i.e. commonly available tools and aids or parts thereof made by other suppliers are not part of the WORK.

### Special instrumentation

The CONTRACTOR shall supply all the special HW and SW instrumentation required for the operation and maintenance of the WORK.

This is especially the special instrumentation required for operation and maintenance, special instrumentation meaning devices specially made for the equipment supplied by the CONTRACTOR. This equipment shall also include special SW products needed for the above purposes, including licenses for installing on standard media and computers, regardless of whether or not these devices and computers are part of the WORK.

This equipment shall include, among other things, the full assortment of special instrumentation that will be used by the CONTRACTOR for testing, commissioning, operation and troubleshooting. This means that the CONTRACTOR will not use other kinds and types of instrumentation other than those concurrently supplied by the CONTRACTOR for this purpose. Special instrumentation shall be delivered in the numbers and types corresponding to the usual maintenance method.

The manner of using the special instrumentation shall be an integral part of the training of the PURCHASER’S administration, operation and maintenance staff and shall also be described in the maintenance work procedures.

Special instrumentation shall be delivered including work procedures for inspection and maintenance.

## Supply of services and works

Supplied  SERVICES and WORKS shall include SERVICES AND WORKS referred to in items (a) to (z) of Chapter 2.1 above, while respecting the requirements and conditions specified in the CONTRACT for their implementation, and in particular:

Collaboration in resolving possible conflicts between the WORK and the follow-up projects.

Participation of CONTRACTOR'S representatives in consultations and coordination meetings with the suppliers of the follow-up projects convened by the PURCHASER.

Other obligations of the CONTRACTOR:

- - in the field of external environment aggressiveness:

• perform measurements of the current field and presence of stray currents,

• measure soil resistivity (Ω.m) and determine its corrosive aggressiveness in the space of buildings of this construction project,

• determine and incorporate measures against stray currents for all structures and equipment threatened by stray currents,

• perform basic chemical analysis of groundwater, classification of groundwater and rocks in terms of corrosion aggressiveness for concrete structures,

• design and implement access to surfaces with corrosion-resistant treatment to inspect the status of  the anticorrosive treatment,

• elaboration of Protocols on determination of external influences for all premises and rooms of this construction project according to ČSN 332000-5-51 ed.3, as amended.

- - in hydrogeology:

• verification of steady groundwater level.

• performing basic chemical analysis of groundwater, classification of groundwater and rocks in terms of aggressiveness to concrete.

## Software user rights

Licenses and RIGHTS OF USE will be dealt with in compliance with Section 17 of the CONTRACT.

- Licenses and RIGHTS OF USE granted by the CONTRACTOR in accordance with and under the conditions set forth in Section 17 of the CONTRACT shall also include licenses and RIGHTS of USE for the supplied software, with the WORK including in particular:

Supply of all system software for programmable technical devices (SW performing all standard functions of the control system and allowing communication within the system - operating systems, firmware) including original installation data media.

Supply of all application software for supplied programmable technical devices (SW created specifically for the solution of specific functions necessary to execute the WORK), including original installation data media.

Performing modifications of the application SW of the existing control systems, instigated by the execution of the WORK.

Supply of all software resources necessary for testing, trials, maintenance, modification and further development of supplied programmable technical means, including  licenses for their use.

Performing modifications to the application software of the new SKŘ, as required by identified deficiencies during the tests, COMMISSIONING, TRIAL OPERATION and in the WARRANTY PERIOD. The WORK shall also include changes in the SW to the extent of 20% of the source files of the entire application SW, instigated by reasons on the part of the PURCHASER, for example, additional PURCHASER’S requirements for SW changes resulting from operational experience gained prior to the expiration of the WARRANTY PERIOD.

# Work boundaries

The outer boundaries of the WORK (supplies) are the boundaries between the WORK and the intact "surroundings" of the WORK where " surroundings" means, within the meaning of this and other similar provisions, the following:

Buildings, constructions, roads.

Machinery, piping systems.

Electrical equipment including existing sources for powering the WORK.

SKŘ, communication networks.

Other connected facilities.

The EXTERNAL LIMITS of the WORK are set out as shown below for each area.

The boundaries of the CONTRACTOR'S design work are generally the same as the supply boundaries.

The locations of the connection points are evident from Amendment D01 and Amendment D05.

| CP Number | Purpose | Parameters | Connection Point |
| --- | --- | --- | --- |
| NB 1 | Lime to agglomeration mixing center | Lime: DN 110 PN-91/M-51038 Air: C-DIN 2 ½“ | Filling neck of existing lime silo No. 4 |
| NB 2 | Limestone for limestone suspension preparation | Limestone: DN 110 PN-91/M-51038 Air: C-DIN 2 ½“ | Filling neck of existing limestone silo No. 2 |
| NB 3 | Limestone for limestone suspension preparation | Limestone: DN 110 PN-91/M-51038 Air: C-DIN 2 ½“ | Filling neck of existing limestone silo No. 3 |
| NB 4 | Saline water for limestone suspension preparation | PE 225x20.5 | Main saline water distribution system |
| NB 5 | Lime to agglomeration mixing center | 800x600 | Mixer inlet – inlet part of supply |
| NB 6 | Water from collection tank to agglomeration | DN150, PN16 | Mixer inlet – pre regulation flange |
| NB 7 | Gypsum suspension to agglomeration | 800x600 | Mixer inlet – inlet part of supply |
| NB 8 | Flue gas for desulfurization | 2x(4000x1916) 3x(4000x1199) | Flue gas dust to absorber |
| NB 9 | Flue gas dust into existing dry stack | 2x(4000x1916) 3x(4000x1199) | Flue gas dust into existing dry stack |
| NB 10 | Raw water | DN300 | Main raw water distribution system |
| NB 11 | Air for technology instrumentation and control equipment | 3.5bar DN500 7bar DN250 | Main distribution system in boiler room |
| NB 22 | Flue gas to LF K6 | 8x(1250x1250) | Inlet flanges of inlet flaps to LF K6 |
| NB 23 | Flue gas from LF K6 | 8x(1400x500) | Outlet flanges of outlet flaps to LF K6 |
| NB 24 | Flue gas to LF K7 | 8x(1250x1250) | Inlet flanges of inlet flaps to LF K7 |
| NB 25 | Flue gas from LF K7 | 8x(1400x500) | Outlet flanges of outlet flaps to LF K7 |
| NB 26 | Flue gas to LF K8 | 8x(1250x1250) | Inlet flanges of inlet flaps to LF K8 |
| NB 27 | Flue gas from LF K8 | 8x(1400x500) | Outlet flanges of outlet flaps to LF K8 |
| NB 28 | Flue gas to LF K9 | 8x(1250x1250) | Inlet flanges of inlet flaps to LF K9 |
| NB 29 | Flue gas from LF K9 | 8x(1400x500) | Outlet flanges of outlet flaps to LF K9 |
| NB 30 | Flue gas do LF K10 | 8x(1250x1250) | Inlet flanges of inlet flaps to LF K10 |
| NB 31 | Flue gas from LF K10 | 8x(1400x500) | Outlet flanges of outlet flaps to LF K10 |
| NB 32 | Ash from K6 | DN150 | Pneumatic ash transport route from K6 outlet flange of ash container |
| NB 33 | Ash from K7 | DN150 | Pneumatic ash transport route from K7 outlet flange of ash container |
| NB 34 | Ash from K8 | DN150 | Pneumatic ash transport route from K8 outlet flange of ash container |
| NB 35 | Ash from K9 | DN150 | Pneumatic ash transport route from K9 outlet flange of ash container |
| NB 36 | Ash from K10 | DN150 | Pneumatic ash transport route from K10 outlet flange of ash container |
| NB 37 | Heating and return water for SO 02 | 2x DN65 | Existing pipe systems of heating and return water |
| NB 38 | Heating and return water for SO 01, SO 04, SO 05, SO 09 | 2x DN125 | Existing pipe systems of heating and return water |
| NB 39 | Raw water to saline water tank | DN300 | Existing raw water filter |
| NB 40 | Sewer system | DN700 | Existing sewer system |
| NB 41 | Water system | DN100 | Drinking water distribution system in boiler room |
| NB 42 | Fire water |  | Distributor at boiler K5 |
| NB 43 | Heating and return water | DN100 | Branch from main distribution system |
| NB 44 | Electrical power for connecting new vn distribution boards | 3PE AC 50Hz 6 kV/IT | Busbars in two reserve cells of existing substations R6KYI and R6KYII |
| NB 45 | Electrical power to supply 5pcs of circulating pumps and booster combustion air fan | 3PE AC 50Hz 6 kV/IT | Busbars in six reserve bays (fields) of existing substations R6KYI, R6KTI |
| NB 46 | Electrical power to supply new loads in limestone management | 3PEN AC 50Hz 400/230 V/TN-C | Existing distribution board 00BFA |
| NB 47 | Control system K6 – K10 | Honeywell Experion PKS | Boiler room +7.7 m: K06 – switchboard P06 K07 – switchboard P07 K08 – switchboard P08 K09 – switchboard P09 K10 – switchboard P10 |
| NB47a | Control system Joint operation of K06 - K10 | Honeywell Experion PKS | Boiler room +7.7 m: K00 – switchboard 0CJJ01 00CJJ02 |
| NB 48 | Control system pneumatic transport and limestone silos | Rockwell Automation | Below limestone silos: Switchboard - 32CJA01 |
| NB 49 | Control system dry ash loading station | Siemens S7-1200 | Boiler room +17 m for boiler K10: Switchboard– 10ETG30GS001 |
| NB 50 | Control system electrical equipment | Micro SCADA | Control room - electrical |
| NB 51 | Emission monitoring | Orgrez SW - EISORGNET with ESEP evaluation | Central control room |
| NB 52 | Telephone lines | Existing telephone switchboard | Existing server room (see Amendment D05) |
| NB 53 | Company network | Existing switch | Existing server room (see Amendment D05) |
| NB 54 | EPS | LITES MHU111 | Exchange – in building 30 (Fire station) Concentrators – in building 33 (Small spare parts storage) |
| NB 55 | LF fly ash from silos | Filling neck of tank 35 – 50 m3 | 2x outlet orifice for filling holes 450 mm |
| NB 56 | Dewatered energo gypsum | Dump truck/semitrailer truck+trailer 24-50 m3 | Output conveyor (equipment) for loose material loading |

Note: Connection points NB 12 - NB 21 are not boundaries of the WORK.

# Requirements for work technical design

In the specific technical design solutions, it is necessary to take into account the requirements of the PURCHASER referred to in this chapter; however, other requirements of this Supplement 1 to the CONTRACT, such as the requirements for the basic parameters of the WORK (Chapter 1.6.4), the operational requirements (Chapter 5), the maintenance requirements (Chapter 6), the service life requirements of the installation (Chapter 7), as well as other requirements set out in other CONTRACT documents.

## Basic requirements for the entire work

Proven process and equipment

The WORK shall be based on technology whose operational reliability has been verified in continuous operation and which establishes a prerequisite for meeting the qualitative and performance WORK warranties under the provisions of the CONTRACT.

The work must be carried out in accordance with Amendment D01 (Zoning Permit Documentation - DUR) as waste free technology – closed circuit (regarding water).

All GOODS, i.e. machines, equipment and apparatuses, unless otherwise stated in other  CONTRACT provisions, shall be of proven design, first-class quality, verified and proven by references. All types of equipment must be suitable for the purpose, operationally verified, highly efficient, safe, designed and manufactured in accordance with ČSN or internationally accepted standards (unless otherwise specified) and procured from experienced and reliable manufacturers who provide service maintenance of the supplied equipment in Czech Republic. Suitable design shall prevent leakage of operating substances (e.g. from seals of pumps, mixers, etc.), all leakage of the operating substances shall be contained and returned back to the process or disposed of properly.

The accessibility of the individual equipment items for maintenance must be simple, without the need to dismantle other equipment.

Low maintenance costs

Maintenance costs must be as low as is reasonable and achievable, provided that the intended outcome, in terms of service life and availability, is not affected. These general requirements shall be reflected in the process technology, construction and standardization of the equipment, the general and detailed structuring of the WORK.

Low operating costs

The equipment shall exhibit low mass, energy and water consumption when meeting the specified capacity and complying with all qualitative parameters, in accordance with the requirements of the CONTRACT. This requirement also means optimizing the design concept of the whole WORK in terms of emission reduction efficiency and in terms of consumption of electricity, operation consumables, and all water types.

Process safety

The WORK shall be designed and delivered so as to limit the risks arising from the process. The process must be safe and all necessary precautions must be taken to avoid danger to personnel, equipment and the environment during the start-up, normal operation, planned shutdowns, emergency shutdowns and outages. At the same time, the work must comply with all safety regulations, requirements resulting from the DSP and the requirements of the permitting authorities.

Standardization

The CONTRACTOR must strive to standardize the equipment as far as possible in order to rationalize the operation and maintenance of the WORK, and reduce of the number of spare parts. It is recommended to provide the same kind and type of equipment from one manufacturer. This applies, for example, to pumps, fittings, electrical motors, control systems, connecting material, flange joints, etc. However, this must not have a negative effect on the function, cost and operational reliability of the equipment.

Single marking system

All labels of newly supplied constructions, systems and components shall be made in a uniform manner in accordance with the KKS identification system - see Chapter 1.11.

Emission limits

Emission limits must be respected in the long-term operation and at various wear levels of the sub-assemblies over their service life (e.g. recirculation pumps, spray nozzles, lamellas, droplet separators).

## Civil part requirements

When implementing the civil components of the WORK, the CONTRACTOR shall comply with all the requirements and conditions arising from the CONTRACT and its Supplements.

The CONTRACTOR shall provide detailed design for the solution and execution of each SO, taking into account the needs and requirements of the installed technology, respecting the basic and restrictive conditions of the construction project and other conditions and requirements stated in this Supplement 1 to the CONTRACT and in other documents of the CONTRACT.

The design of all construction structures shall be carried out in accordance with the standards and regulations in force in the Czech Republic, including the regulations for the fire safety of the WORK and operating regulations related to work safety.

When designing structures, the local conditions will be reflected - geological conditions, climatic conditions, corrosive nature of the environment, etc.

The design of new structures shall reflect the current state especially of the foundation structures of the adjacent and connected structures. When working in the vicinity of the existing buildings, these structures shall not be compromised and damaged by this construction work.

Fire escape routes shall be designed in accordance with fire-protection  design of the structures.

Based on the fire-protection technical design, ladders shall be installed on roofs of buildings, dry-risers, firewalls, etc.

### Applicability of project documents

The external shape geometry is mandatory according to Amendment D01, the designated construction site must be observed vertically and spatially. The internal configuration and layout is informative and does not have a binding character. The specific solution depends on the CONTRACTOR and must suit the requirements of the machinery and related equipment.

The material and design solutions are a matter of the CONTRACTOR under the condition that the CONTRACTOR proposed solution shall have the same or better parameters than those specified by the PURCHASER in this document.

### Basic requirements

#### Requirements for geometric deviation of structures

The required tolerances are defined by the surveying precision in construction according to the appropriate standards. If the installed equipment and connected systems require stricter requirements in order to ensure their proper functioning, it is the obligation of the CONTRACTOR to ensure these.

#### Structural and static requirements

Unless otherwise specified, the following requirements shall be met:

Load bearing capacity

The initial values ​​for determining the bearing capacity of the subsoil are the values ​​indicated in the engineering geological survey, except each case, where these parameters shall not be in agreement with the data obtained during verification tests performed directly at the CONSTRUCTION SITE.

Tilting

No part of the foundation structures shall have a tendency to lift either by the effect of loading or stress of any nature.

Horizontal forces

Pile foundations must be dimensioned to safely withstand all forces (horizontal load, bending, negative friction, etc.).

Settlement

If stricter values ​​are not required by standards or requirements to ensure the correct function of the equipment, the design limit values ​​for the foundation structures settlement shall be as follows:

Final total average settlement 25 mm;

Differential settlement (relative difference) 5 mm.

In no case the settlement values ​​shall exceed the limits that would prevent or limit the proper functioning of the installed equipment, installations and technology, including their interconnection and media distribution.

Joint control

When designing concrete structures, the following requirements must be met:

Controlling joints and cracks considered to be particularly undesirable because of the impact on the functionality and service life of the following structures, equipment and spaces:

All storage spaces;

Tanks with reactive substances;

Exhaust pipes and stack for flue gas discharge;

All areas with requirements for liquid impermeability;

Below ground-level structures that must be watertight with respect to pressurized or non-pressurized water;

Walls of buildings threatened by water vapor condensation;

Walls of structures exposed to aggressive environment.

The following conditions must satisfied:

The permissible joint width, depending on the aggressiveness of the environment, must not exceed 0.2 mm for the combination of quasi-static loads (according to the provisions of the European standard ČSN EN 1992).

Control of joints considered undesirable with respect to the operation and service life of other structures must satisfy:

The permissible joint width, depending on the aggressiveness of the environment, must not exceed 0.3 mm for the combination of quasi-static loads (according to provisions of the European standard ČSN EN 1992).

Earth pressure

In addition to earth pressure and groundwater pressure, all loads caused by heavy machinery and vehicle movement loads and loads resulting from the interaction of the foundation structures of the surrounding structures must be considered.

Groundwater pressure

The least favorable groundwater level must be determined when designing and assessing structures for the impact of groundwater pressure.

The stability of structure must be verified for an empty building.

#### Loading

Permanent loading

The respective permanent loads shall be determined for each design situation according to ČSN EN 1990 ed.2. The total own weight of the load-bearing and non-load-bearing elements shall be considered in the load combinations as an independent load.

In designing and assessing the structures, the effects of loading of building structures and permanently installed equipment shall be considered. In the design, critical load states shall be determined in those areas where load bearing or non-load bearing elements are to be removed or added.

The loading for storage areas shall be determined on the basis of the unit weight and the design upper height value ​​of the stored materials. For bulk materials, source and moisture content shall be defined in design situations. If the stored material generates horizontal forces on walls, etc., these forces shall be reflected in the calculations.

In the respective design situations, water level and earth pressure shall be considered.

- Random loading

- The respective random loading shall be determined for each design situation according to EN 1990 ed.2.

- In designing and assessing the structures, the effects of payloads resulting from building usage shall be assessed.

- In addition to the aforementioned loading, the following shall be verified:

Dynamic effects of all equipment and equipment;

Additional loading induced by heavy vehicle movements;

Additional loading induced by lifting and handling equipment;

Additional loading induced by installation and maintenance of devices and equipment;

Tension caused by temperature changes, shrinkage, construction creep and tension introduced by supports subject to dimensional changes in the technical infrastructure networks;

Loading of seismic origin.

Extreme loading

When designing and assessing structures, any unexpected operating, testing and emergency situations that may occur (e.g. sudden shutdown of machines) shall be reflected in the calculations.

Climatic and seismic loading

When designing and assessing structures, the effects of wind, snow and ice, as well as the effects of natural and technical seismicity and undermining shall be assessed, if the risk impends.

#### Material and execution concept

The concrete constructions shall be designed from structural concrete of the prescribed class, if necessary water-resistant concrete with an additive shall be used. In an aggressive environment, concrete with adequate resistance shall be used depending on the groundwater chemistry.

When casting the concrete mixture, the CONTRACTOR  shall apply:

Joint control plates;

Insulation of work joints;

Watertight caps of formwork spacers.

Unless required otherwise by standards and regulations, the PURCHASER requires B500B construction steel coupled rebars.

The adverse effects of concrete shrinkage shall be limited by a suitable reinforcement arrangement, for example by installing the reinforcement in the compression area of ​​the ceiling, by suitable concrete casting technology (shrinkage strips), maintaining process discipline, quality treatment of the installed concrete, suitable composition of the concrete mixture, and possibly using concrete attaining the required properties after ninety days (e.g. C25/30 90). The standard concrete used shall attain the required properties after 28 days from casting of the concrete mix. For both plates and walls, the horizontal reinforcement shall be designed for a joint width from forced strains.

Unless otherwise specified by standards and regulations, the PURCHASER requires load bearing  masonry from bricks of P10 to P20 quality on MC10.

Unless otherwise specified by standards and regulations, the PURCHASER requires the use of structural steel S235, S355.

The surface coating of steel structures shall be carried out by the CONTRACTOR by hot dip zinc galvanizing. The respective coating system shall be selected according to the aggressiveness of the environment and the requirements of the fire prevention design.

#### Aesthetical and functional requirements

The CONTRACTOR shall comply with the following requirements:

Aesthetic requirements

The construction shall be carried out in an industrial area without any major requirements for the architectural visual qualities.

Functional requirements

The layout of the supporting pillars and beams must not adversely affect the functionality of the equipment and installation;

All measures to ensure the internal working environment, safety and health of employees and possible visitors (communication and escape routes, walking distances) shall be applied;

Individual rooms shall be easy to maintain;

All equipment and installations shall be readily accessible ideally from all sides, serviceable and repairable;

There must be enough space around the equipment for handling and the possibility of repair and replacement, including transport, must be maintained;

Transport and road areas shall be designed in terms of safety and accessibility even in exceptional or emergency conditions, regardless of weather conditions.

The following basic design and safety principles shall also be respected in designing the WORK:

Preference for natural lighting and room ventilation;

The need to protect from sun irradiation;

Ensuring the quality of the indoor environment by controlling air parameters by the air-conditioning, ventilation and heating equipment;

Reduction of energy intensity by the functional use of natural and artificial lighting and ventilation with mutual regulation;

Quality sound insulation and complying with the indoor and outdoor requirements;

Structural components exposed to intensive handling operations shall be protected from impact;

Window cleaning is preferred from the inside of the building, not from a washing platform outside the building;

All roofs where equipment and installations requiring maintenance shall be installed, shall be provided with rails, although not being  walk-in areas;

All areas and roofs of buildings shall be accessible and a safe maintenance and control system shall be designed;

Dead end corridors shall be marked with escape direction.

QUALITY REQUIREMENTS FOR INDOOR ENVIRONMENT

Design temperatures and parameters of the indoor environment shall be determined according to the set of standards ČSN 73 0540 Thermal protection of buildings.

Workplace lighting shall be in accordance with Government Decree No. 361/2007 Coll. to meet the requirements of visual acuity, comfortable visibility, and employee safety in compliance with normative values.

Other sanitary requirements

Depending on the type of room and position of  the workplace, other sanitary requirements such as washability, protective showers, eye showers, clean/dirty facilities, clean/dirty work and civilian clothing, waste management system, etc. must be complied with.

### Structural design of buildings

#### Survey work

The CONTRACTOR shall provide survey coordinate connection to the national system and delineation of all structures of the WORK by a surveyor and an officially authorized surveying engineer. The xy position coordinate system shall be S-JTSK. To determine the elevation of the WORK, the nation-wide Baltic vertical reference system after compensation (Bpv) shall be used. Elevation points inside buildings shall be made in sufficient quantity at a height of +1.000 m above the finished floor. Invalid point and elevation marking shall be entirely removed.

The CONTRACTOR shall ensure in particular:

Co-operation of the surveyor and officially authorized surveying engineer;

Delineating the perimeter of the CONSTRUCTION SITE as defined by the DESIGN;

Stabilization and marking of local survey network points by markers, their xyz survey to determine the position and height. The PURCHASER shall provide information on the existing local survey network in the premises of Teplárna Komořany;

Elaboration of the local survey network documentation (survey data points, list of coordinates, network point layout);

Protecting these points against damage or pollution during construction work;

Checking the network layout points during construction activity;

Establishing the spatial position of the WORK in accordance with the drawings approved upon issuance of the zoning permit decision, the issuance of the building permit and the decision on construction changes prior to project completion. The CONTRACTOR shall provide, if necessary, a copy of the local survey delineation drawing, if the drawing of the valid project design is not sufficiently precise and unambiguous;

Delineate the routes of the existing underground technical infrastructure utilities, based on the documentation and documents of the owner (operator), if they can be impacted by the construction activity. The CONTRACTOR shall always indicate the predicted (estimated) positional uncertainty in the protocol;

Delineation of the layout and dimensions of the WORK objects;

Checking of the dimensions of selected geometric parameters of the WORK by surveying methods, measurement of position changes of  structures as required by the DESIGN;

Measurement of the as-built spatial position and the shape of the WORK and the preparation of the surveying report (drawings, maps), WORK as-built documentation, including the final cadastral site plan.

This inventory is incomplete, the CONTRACTOR shall ensure that the work carried out is in accordance with the effective legislation of the Czech Republic and the technical standards, as amended.

#### Demolition work

Demolition work may be carried out only without limiting the operation of the heating plant.

#### Earth and foundation work

The CONTRACTOR shall provide in particular:

Detailed engineering-geological survey needed to carry out the work, the PURCHASER shall provide information from the previous investigation work on the premises of Teplárna Komořany;

Corrosive properties survey;

Selection of an appropriate method for carrying out earthwork, taking into consideration local conditions, structural design of existing buildings, operational, technical, economic and safety factors;

Stability of excavation walls, regardless of their depth, including drainage of the cut by vertical drainage, concurrently with the gradual excavation of the construction pit;

Executing the necessary earth moving to create operation surface for drilling rigs;

Execution of boreholes for pile and brace walls and for the execution of piles and braces;

Implementation of pile and brace anchoring concurrently with the gradual excavation of the construction pit;

Excavations for all structures that will be built, including spreading and compaction of gravel on the running surfaces;

Backfilling of space around constructed buildings, creation of embankments and beds of paved areas;

Removal of excess excavated soil from the CONSTRUCTION SITE, including the creation of necessary in/out accesses/exits to/from construction pits;

Provide, operate and remove equipment necessary for the execution of works;

Establishment of areas needed to transport, operate and park the equipment necessary to carry out the works;

Establishment of access roads and parking places;

Drainage of the construction pit, drawdown of ground water level;

Compaction to the prescribed state;

Delivery and installation of backfill material;

Removal and disposal of excavated material not used for backfilling, complying with the effective legislation of the Czech Republic;

The performance of work by a qualified work team in accordance with the provisions of the given technological process and with the consistent use of collective and personal means of protection.

This inventory is incomplete, the CONTRACTOR shall ensure that the work carried out is in accordance with the effective legislation of the Czech Republic and the technical standards, as amended.

For earthwork generally, the CONTRACTOR shall be able to use also the excavated material and the recycled material from demolition, with prescribed structure or possibly the existing stabilizate of the PURCHASER and taking into account the technical conditions. If this material will not meet the criteria for material suitable for backfilling, the CONTRACTOR shall ensure the delivery of high quality backfill material.

The material shall have characteristics corresponding to the specific use prescribed by the DESIGN, given conditions and technical regulations (engineering geology survey, standards, technological conditions, safety measures, etc.).

During the processing and after installing of the material into the earthwork structures, its properties shall be verified and proved by the tests prescribed in the DESIGN, standards and related technical regulations.

The suitability of the backfill material shall be assessed and determined by the CONTRACTOR with regard to the conditions for subsequent final use (i.e. biological reclamation, sowing, grassing) and taking into account the purpose, location and technical conditions of use.

Inappropriate and fundamentally unsuitable materials, taking into account the technical conditions of use, are:

Frozen, rain or snow-soaked piled soil consisting of cohesive soils (clays, loams, loess);

Loose soil not complying with the technical and biological conditions of use;

Loose soil of variable properties whose moisture content does not correspond to the required range.

#### Roads and paved areas

The construction of roads, including the installation of prefab components and the installation of the traffic signs, shall be part of the WORK, with a design structure meeting the traffic load requirements according to the relevant standards and the technical certificates.

#### Structures

Wall structures

All brick structures shall be constructed by the CONTRACTOR by using a system solution. Lintels of holes and additional fitting pieces shall be part of the masonry system. In the absence of components with sufficient load bearing capacity, reinforced concrete or steel elements shall be used. Mixed masonry shall not be accepted by the PURCHASER.

Brick constructions shall be designed according to the set of standards ČSN EN 1996 and related standards.

Concrete structures

Concrete shall be imported or produced directly at the CONSTRUCTION SITE. The composition of the concrete mixture shall meet the requirements of the EN 206 standard, based on specific conditions, i.e. the degree of impact to which the concrete shall be exposed in the given environment (e.g. aggressive vapors, condensates).

Concrete reinforcement shall include all types of reinforcement and necessary construction components, including spacers. When using steel as a reinforcement, the CONTRACTOR shall ensure good mutual cohesion, necessary anchoring lengths and reinforcement overlap, required thickness of the cover layer with regard to the specific conditions and fire resistance, the principles for reinforcement design shall also be adhered to.

The quality and structure of the formwork surface shall be governed by the relevant provisions of the standards. The formwork will be carried out by the CONTRACTOR including all reinforcement elements. Edges shall be cambered by insertion of triangular strips. The WORK shall also include the construction of a eaves at the ledges and awnings and filling the mounting holes.

The WORK shall also include all holes and grooves for the installation of wiring, holes for rail anchoring, lift structures, installation holes, blinds control apertures, etc. Additionally also the installation of required anchoring elements for the following installation of technological, machine and transport equipment, construction, steel, locksmith's or joinery construction elements and anchoring elements for the perimeter skin.

Waterproof concrete shall be required for structures that are or could be subjected to long-term one-sided exposure to water pressure.

These include in particular:

Liquid storage;

Construction below ground water level;

Sumps and tanks;

Engineering utility networks and tunnels;

Construction of waterworks (pumping station, etc.).

Prior to covering the structures, the CONTRACTOR shall provide proof of impermeability of the structures for which this property is required.

Concrete structures shall be designed according to the set of standards ČSN EN 1992 and related standards.

Steel structures

The supply of steel structures shall include manufacturing documentation, production, storage, transport and material handling.

All welds on steel structures shall be ground by the CONTRACTOR smoothly and leveled by a filler before the base coat is applied.

Welding work shall be carried out by authorized persons within the meaning of the applicable legal regulations and standards.

The supply of steel structures shall also include the supply of surface treatment by galvanizing in the thickness of 100 m, priming and finishing, including fire protection coating with guaranteed anticorrosive protection of minimum 10 years.

The composition and resistance to external influences of the surface coats shall reflect the respective category of aggressive conditions at application location and the requirements of the fire protection design.

The steel structures will be supplied by the CONTRACTOR including all anchoring and fitting elements.

The steel structures shall be designed according to the set of standards ČSN EN 1993 and the related standards;  welding checks are necessary as required.

#### Completion

Outer skin

The CONTRACTOR´S supply shall include the primer and final coating, coating of the required color shade, all the bearing grates that will be an integral part of the system facades.

The outer skin shall meet the thermal and technical requirements according to the set of standards ČSN 73 0540 Thermal protection of buildings at the time of the DESIGN development.

The type of material used shall be based on the requirements for thermal, mechanical and technological properties at the specific location of installation, including compliance with fire prevention design.

The design of the thermal protection system shall include calculations and verification of the construction details regarding the possible presence of thermal bridges and the occurrence of condensation of water vapor in structures or on their surfaces.

In the event that condensation of water vapor cannot be avoided, the CONTRACTOR shall take steps to control its occurrence, including the protection of exposed structures and condensate drainage in order to avoid degradation of the material, including surrounding structures.

The outer skin shall will be equipped with all fittings, safety devices, glazing, sealing joints between the frame and the building structure, all vertical and horizontal contact and other thermal insulation, including potential vapor barriers or other waterproofing. All skirting, expansion, corner and transition bars of the outer skin shall be supplied.

All materials used shall be certified for use in the proposed structure. The CONTRACTOR shall reflect mutual compatibility of used materials.

Infill of holes and openings

Completed infill of holes and openings shall meet the requirements of the following standards, as amended:

ČSN 73 0540-2 Thermal protection of buildings - requirements;

EN 14351-1 Windows and doors;

ČSN 74 6077 Windows and doors - Requirements for Installation.

Infills of holes and openings shall be provided with all the accessories and supplements to ensure the functionality of the PS and TZB systems.

They will also meet the requirements of:

Fire resistance;

Impermeability to smoke;

Mechanical resistance and stability;

Thermal insulation;

Sound insulation;

Air permeability;

Waterproofing;

Resistance to wind load;

Burglary protection.

Windows

Interior windows

Aluminum frame construction, powder coating, flat float clear glass min. 4 mm, anodized light metal fittings.

Exterior windows

Aluminum frame construction, powder coating, interrupted thermal bridge profiles, double insulating glass pane, "warm" spacer frame, anodized light metal fittings, external window sill from anodized aluminum, inner sill water resistant laminated splinter board.

Glass facades

System of profiles, seals and accessories for vertical façade structures. In interior supporting steel profiles hot dip galvanized, in exterior aluminum cover strips.

Interruption of thermal bridge on the principle of sealant free glazing.

Doors and gates

Interior doors

Minimum clear dimension 800/1970 mm, galvanized steel, splinter board inside, powder-coating/ plastic sheet, frame - galvanized steel, with powder-sprayed basecoat, interior fittings metal, cylinder lock, door closer, plastic wall mounted stop.

Security doors

Minimum clear dimension 800/1970 mm, galvanized steel, all-metal double-walled inside with longitudinal and transverse reinforcements, powder-sprayed coat/plastic sheet, galvanized steel door frame with powder-sprayed primer, metal safety locks, multipoint security lock, door closer, plastic wall mounted stop .

Fire doors

Minimum clear dimension 800/1970 mm, galvanized steel, inside material according to the required fire resistance, powder-sprayed coating/plastic sheet, metal fire resistant door frame with  peripheral seal and powder-sprayed primer, cylinder lock, door closer, panic handle, sign, plastic wall mounted stop.

Gates

Industrial, in sections, self-supporting construction, motor shaft drive with the possibility of manual operation by chain, steel double walled galvanized, finish powder-spray coat, mechanically resistant, sealing on four sides along perimeter and in-between the door sections, partially glazed, thermally insulated, with electronic security and access control, protection from lifting, fall and crushing, protection of the lower edge against obstructions or persons, drive with a smooth start (frequency converter). The size of the door shall enable the dismantling and installation of all installed equipment and parts of the technology.

Ventilation grids

Fitted into a façade with a flap connected to the control system, aluminum, protection against rain.

Hatches

Surface treatment against corrosion, folding, mechanical opening, watertight and odor tight seal, loading according to the requirements of the adjacent area (500 kg/m2). Possibility of manual handling.

Waterproofing

The waterproofing elements of the WORK shall be designed by the CONTRACTOR according to ČSN P 73 0600 based on the specific hydraulic and physical stress, the waterproofing class depending on the type of protected area and the accessibility of the waterproofing structures.

The waterproofing of reservoirs, sumps and tanks exposed to a chemical aggressive environment shall be designed by the CONTRACTOR based on the degree of aggressiveness of the environment. The waterproofing system shall preferably be executed by chemically resistant coatings (e.g., a crystallization or epoxy coating). The functionality of the system shall be verified by tightness tests by the CONTRACTOR.

Roof structures within the WORK shall be designed by the CONTRACTOR according to ČSN 73 1901. They will be equipped with a complex system of liner waterproofing based on softened PVC. The selected material shall meet the conditions of resistance to external factors, including heat stress, ultraviolet exposure and acid rains. Expansion joints, interconnections and transitions of individual structures shall be designed using system elements, using the recommended details of the supplier. The roofs shall be constructed with a gradient of 1.0% minimum.

In wet operations (e.g. showers), the CONTRACTOR shall apply waterproofing sealant extending up the wall (minimum 0.15 m, in showers up to 2.0 m height). The waterproofing sealant shall be reinforced in the corners by a reinforcement mesh.

The liner systems shall be installed by the CONTRACTOR inclusive of the complete accessories and tin smith elements made of hot dip galvanized sheets with plastic coating.

All used materials shall be certified for use at the proposed composition. The CONTRACTOR shall reflect the mutual contact compatibility of the materials used.

Acoustic insulation

The CONTRACTOR shall verify all acoustic descriptors (reverberation, speech intelligibility, noise loading, spatial attenuation) with respect to the function of the given rooms (corridors, operating and technical rooms, etc.). The CONTRACTOR shall provide all measures to meet sanitary requirements and comfort of the working environment.

Depending on the requirements for the acoustic properties of the structures, the following shall be used:

Step noise attenuation in flooring layer structure;

Acoustic insulation in the partition wall structures;

Reflective or absorbing acoustic panels to manage reverberation and attenuation;

Attenuation sleeves on utility installations and insulation of installation cores.

In buildings where acoustically protected areas shall be located, the partition structures shall meet the parameters for attenuation and prevention of acoustic permeability and shall meet the sanitary required sound pressure levels at workplaces.

##### Vibration and shock damping

The CONTRACTOR shall design and assess any equipment producing dynamic effects with potential negative effect on the functionality, reliability and safety of the installed equipment, the mechanical resistance and stability of the surrounding structures and the sanitary requirements required by the legislation as amended.

These are in particular the following:

High performance fans on block foundations;

Piston or rotary compressors and blowers, usually on block foundations or on vibration damping frames;

Transport equipment - cranes, vibratory belt conveyors and lifts;

High performance pumps;

Vibration of pipelines due to turbulence of the flowing media;

Flexible connection of compressors and blowers and parts of technology to fixed pipelines;

Other technological and transport facilities generating dynamic effects.

For the reliable design of structures and foundations carrying equipment producing dynamic effects, the following requirements shall be met:

Requirements for operability:

Limit criteria for mechanical vibrations under steady forced oscillation at the foundations of rotating machines or their non-rotating components (especially at bearing locations of rotating systems) according to the requirements of the supplier (manufacturer) of the equipment, the relevant standards (e.g. ČSN 12 2011 for fans) or sanitary regulations;

Permissible vibration level of foundations at the location of equipment sensitive to the level of mechanical vibration (e.g. laboratory scales, spectrometers, etc.);

Limit values ​​of oscillation response expected to produce visible failures on construction bearing and non-load-bearing structures;

Compliance with normative requirements for limit vibrations at the workplace and in protected areas of buildings, as stipulated in the Government Decree No. 272/2011 Coll. on the protection of health from the effects of noise and vibrations;

Structures on which the equipment shall be installed and connected must not resonate with the operating speed of any machine component or technological distribution system components.

- Bearing capacity requirements:

Response amplitudes of internal forces or stress in the structure, as established by a dynamic calculation when considering maximum dynamic loads, shall be evaluated.

Design assessment for high-cycle fatigue stress.

Elastomer or neoprene bearings and spring vibration isolators shall be used to dampen vibrations and vibrations.

The functionality of damping bearings and spring insulators shall be ensured even in the event of a fire.

The CONTRACTOR shall design such measures as to eliminate undesirable vibrations, to ensure the required sanitary values at the workplace in the protected areas with regard to vibrations. Workplaces where such parameters cannot be attained must be dealt with by instituting operating rules in accordance with the sanitary regulations.

### Requirements for technical equipment of buildings  – TZB and infrastructure networks

Requirements for internal networks of technical Infrastructure:

The WORK shall include the supply of necessary certificates of products, pressure vessels, pressure and operating tests, adjustment and regulation of all systems, including provision of protocols, operating regulations and operating rules, provision of inspection reports, instructions in the Czech language and training of operators.

The WORK shall include the supply and installation of all the thermal, fire protection and acoustic insulation of the technical infrastructure lines.

The CONTRACTOR shall properly anchor all distribution systems and their terminals  and provide and install suitable elements ensuring expansion in length or volume. The anchoring and compensating elements shall be provided with surface finish ensuring sufficient corrosion and fire resistance throughout the proposed lifetime.

The  CONTRACTOR shall ensure that all TZB and associated distribution systems shall be protected against harmful transmission of vibrations to the surrounding structures and against the emissions of excessive noise according to valid standards and legislation.

The installed distribution systems shall be visibly and orderly arranged in the installation troughs and bridges.

In reinforced concrete structures, the ducts shall be conducted through pipes and boxes designed for inclusion in formwork and subsequent concrete casting.

All parallel lines and crossings of individual installations shall be installed according to valid standards.

The CONTRACTOR shall provide media flow marking on the pipelines, marking on wiring including sockets and ports, accesses, operating pressure and settings, pump setup to specified speeds, fire flaps, and supply of and information system required for trouble-free operation and proper maintenance.

The CONTRACTOR shall route, conduct and interconnect the internal wiring, design its material composition, install cleaning and inspection fittings and provide conformance reports according to valid regulations and standards. The CONTRACTOR’S design must provide a system solution with straight lines, simple and reparable, for example, by routing through installation cores or troughs.

- Requirements for external network technical infrastructure:

Prior to the commencement of earthwork, the CONTRACTOR shall ensure surveying of all underground utility networks concerned and the identification of their position in the field, including their identification.

All earthwork shall be carried out by the CONTRACTOR according to valid standards, regulations of local authorities and according to the requirements of administrators of individual networks.

The WORK shall include the excavation, lagging, bed fills, laying of pipes, including all fittings, pipe fittings and inspection manholes, the implementation of warning and protective layers, the execution of concrete works, providing filling and pipe backfill and their compaction, removal of material to a landfill, surface recovery to original condition.

Crossings and parallel runs of the designed cable routes with other underground utility networks shall be carried out by the CONTRACTOR in accordance with ČSN 33 2000-5-52 ed.2 and ČSN 73 6005. At the road crossings, the utilities shall be enclosed in a protective tube.

Utility protection tubes under roads shall be made of non-corroding material.

The CONTRACTOR shall provide utility connections with an identification tag and a warning liner that will be laid over the pipe.

The material shall have the characteristics corresponding to the specific use prescribed by the DESIGN and reflect the local conditions and technical regulations (engineering geological survey, standards, technological conditions, safety measures, etc.).

During processing and after incorporation of the material into the earth structures, the CONTRACTOR shall verify and prove its properties by tests prescribed in the DESIGN, standards and related technical regulations.

Backfill material shall be used by the CONTRACTOR with regard to the conditions for subsequent final use (i.e. biological reclamation, sowing, grassing) and taking into account the purpose, location and technical conditions of use

Inappropriate and fundamentally unsuitable materials, taking into account the technical conditions of use, are:

Frozen, rain or snow-soaked piled soil consisting of cohesive soils (clays, loams, loess);

Loose soil not complying with the technical and biological conditions of use;

Loose soil of variable properties whose moisture content does not correspond to the required range.

#### sanitary technical installations

Sewer

External sewer system

The sewer connection shall be designed by the CONTRACTOR according to ČSN 75 6101 Sewerage networks and sewerage connections. The route shall be as short and straight as possible in a single slope.

Minimum connection slope:

DN <150 gradient 2%

DN ≤ 200 gradient 1%

Maximum 15% gradient (exceptionally 40% when securing the pipeline against displacement).

The pipes shall be installed by the CONTRACTOR in excavations with regard to the soil composition (sand bed, concrete saddle, concrete saddle with construction site drainage, concrete saddle with gravel/sand bed with construction site drainage), backfill shall consist of fine material to a height of 300 mm above the upper edge of the pipe, after compaction to be backfilled with upper layer.

The sewer connection shall be designed by the CONTRACTOR in sufficient distance from the foundations of the structures and other parallel lines, taking into account the depth of excavation under the grade, the depth of structure foundations below grade and the angle of the internal friction of the soil.

Drainage of paved areas and land shall make maximum use of the terrain grade and use on site drainage. The CONTRACTOR shall provide inspection and cleaning manholes on the pipe system.

Drainage

Drains shall provide drainage of excessive water from foundation structures of both land and utility networks and roads. The CONTRACTOR shall complete them from system components, secure against clogging and allow for inspections and checks. All drains shall be routed to the sewer system.

Ventilation, air conditioning

The incoming ventilated/airconditioned air shall meet the requirements of Government Decree 361/2007 Coll., Laying down the conditions for the protection of health at work. The incoming air shall contain a such proportion of ambient air sufficient to reduce the concentration of gaseous substances and aerosols below the exposure limit values ​​and the maximum admissible concentrations.

For forced ventilation, the incoming air shall be filtered and heated in the winter.

The CONTRACTOR shall design the route, connections, material of the system, and provide it  with cleaning and inspection fitting pieces, flaps, regulating elements and provide conformance reports according to valid regulations and standards.

In rooms with excessive heat generation without permanent presence of operators (e.g. floors with process technology, control systems, substations), the CONTRACTOR shall ensure the indoor environment is adjusted to the required operating temperatures according to the requirements of the equipment. Air-conditioning units with air filtration, cooling or heating shall be installed to ventilate these spaces, which will provide temperature adjusted ambient air on the basis of indoor measurements and maintain a temperature within the specified operating temperature range.

The design of the ventilation system shall respect the requirement for maximum waste heat recovery. The system supplying air to the building shall provide heating of the incoming air in winter by mixing and/or recuperation. Waste heat will also be used to heat rooms without heat originating from equipment.

In the summer, the ventilation of the hall operating spaces shall be supported by wall and roof fans drawing air through the blinds from the outside.

Hot water heating

Hot water heating of the substations and spaces with electrical equipment shall be carried out so that potentially  dripping water is safely drained to places where it cannot disrupt the operation of the electrical equipment.

Electrical installation in structures

In the individual SOs, the indoor electrical installations in buildings shall include the design, supply and installation of heavy and light current systems, grounding, lightning protection, switchboard equipment, lighting and sockets. The installations shall also include electrical wiring for heating, ventilation, cooling and air conditioning of indoor building environments, for sanitary technology, control, monitoring and regulation, power supply for automatic gates and doors and other equipment in buildings.

- The indoor electrical installations must comply with, in particular:

Safety of persons and property;

Operational reliability in the given environment for the particular mode of operation and environmental impact;

Clearly arranged system layout, enabling quick localization and elimination of possible failures;

Easy adaptability of the system for the relocation of electrical equipment and machines, when required;

Economic efficiency in capital and operating costs;

Aesthetic properties;

Prevention of adverse effects and disturbances in crossings and parallel installations with communications lines.

Heavy current wiring

In the individual buildings it shall be used for:

main, backup, emergency (escape) lighting;

socket wiring 230 V, 400 V for occasional use (cleaning and maintenance);

connection of non-technological appliances.

The electrical devices shall be connected by the CONTRACTOR to the main switchboard of the building. From this switchboard, each secondary lighting and motor switchboard shall be connected.

The electrical installation shall include NN switchboards, cabinets (socket, control), separate devices (luminaires, switches, sockets), connecting wiring (cables), storage and protective structures, working and protective grounding.

Grounding

The CONTRACTOR shall provide grounding by a metal strip conductor FeZn, with cross section according to valid technical standards. The grounding resistance of one lead will not exceed 10 Ω. Connections in the ground shall be protected against corrosion. Safety signs shall be installed on the leads, prohibiting presence of persons during storms within distance of 3 m. Connecting strips shall be provided in all technical and machine spaces, elevator shafts and the foundations of the transport equipment.

Voltage compensation

The voltage compensation shall be implemented by the CONTRACTOR according to valid technical standards, by coupling all installed technical systems and conductive technical installations by a connection to the main voltage compensation rail.

Lightning protection devices

All over-ground SOs shall be equipped by the CONTRACTOR with protection against lightning in accordance with the set of standards ČSN EN 62 305, based on the determination of the lightning protection class. Any conductive features of construction on the facade shall be reflected by the CONTRACTOR.

Non-conducting roof superstructures, as well as their technical equipment with electrical connections to the inner part of the building, shall be protected by the collecting rods.

Conductor installations

Conductor wiring shall be carried out by the CONTRACTOR according to the valid technical standards and recommendations of manufacturers. In the design, the CONTRACTOR shall take into account in particular:

Electrical current loading;

Local conditions where conductors are installed;

Bending radii;

Protection against mechanical damage;

Cable routes shall be reliably separated by partitions between heavy and light current conductors. Metal carriers shall be included in the balancing potential.

Switchboards

All switchboards shall comply with the requirements of ČSN  EN 61439. The switchboards shall be supplied by the CONTRACTOR as steel sheet cabinets enclosed from all sides, including a base with a degree of protection reflecting the given operation and the environment according to the international standard IEC 60529, and with all the accessories.

Lighting

The lighting shall meet the requirements of ČSN EN 12665 ​​Light and lighting - Basic terms and criteria for specifying lighting requirements. The design of artificial lighting shall be carried out by the CONTRACTOR on the basis of ČSN EN 12464 Light and lighting - Lighting of work places. Emergency lighting shall be designed by the CONTRACTOR according to ČSN EN 1838 Light and Lighting - Emergency lighting.

The types of luminaires shall be designed by the CONTRACTOR with respect to the type of operation and environment. The nominal current of the luminaires shall under no circumstances exceed the nominal current of the circuit protection instrument. The switches shall be installed by the CONTRACTOR based on the type of wiring, type of electrical distribution, type of material on which the wiring is installed, and the local conditions. The location of the switches shall be 1.2 - 1.5 m above the floor. Switches next to doors shall principally be on the side where the door opens so that they are not covered by the opened door.

The main lighting shall be designed by the CONTRACTOR according to the nature of the work activities and usage of the illuminated spaces, mainly by fluorescent lamps, part of them with emergency modules-converters.

Backup lighting shall be, where suitable for the nature of operations, part of the main lighting, but with separate circuits backed by a backup source

Emergency lighting shall be provided, where suitable for the nature of operations, by main system luminaries supplied by own power source (NiCd-accumulator) or potentially own luminaries with own sources connected to the lighting circuits.

Sockets

Sockets shall be installed by the CONTRACTOR according to voltage, current, type of environment and type of material on which the socket is installed. The number of sockets shall be governed by the requirements of the operation, installed equipment and technology. For permanently connected single-phase appliances with a power input of more than 2 kVA or more, fixed protected separate circuits shall be installed by the CONTRACTOR. Heating units with power consumption of over 2 kVA and appliances from 4.4 kVA will be connected to separately protected three-phase circuits.

The socket wiring shall provide the connection of standard equipment according to operation, housekeeping and maintenance needs. This will include installed appliances with motors: HVAC, sanitary appliances, heating and other electrical appliances of the building.

Backed up circuits shall provide power to several important equipment items in the event of a power outage. Selected equipment shall be connected to backed up circuits powered from the backup power supply in the event of a power outage. This is primarily equipment serving for evacuation, personal and property protection, elevator emergency service, exhaust fans, opening of holes, lifting, handling and testing facilities within the workshops.

Light current installations

The CONTRACTOR shall install in the buildings light current appliances and internal wiring that shall be designed within PS 12 to PS 14.

#### Outdoor lighting

The lighting of roads shall meet the requirements of the set of standards ČSN EN 13201 Road lighting.

Outdoor lighting shall consist of discharge lamps or LEDs mounted on galvanized steel tube poles without anchor base, or on booms on building walls or piping bridges. The lights shall be positioned so that no light smog occurs.

#### Lifting equipment

Crane runways, monorail cranes and mobile structures

The spatial layout, construction design, tolerance, measurement and rectification shall be in accordance with ČSN 73 5130 Crane Runways.

The lifting and assembling equipment shall be delivered part of machine technology.

Freight elevator with passenger transport

Minimum requirements:

Capacity: 1600 kg

Lifting speed: 0.63 m/s

Door opening size: 2.2 x 2.3 m

Cab dimensions: 2.5 x 2.9 x 2.3 m

The elevator cabin finish shall be stainless steel. Protective hardwood impact strips on the side walls of the cabin. Fluorescent lighting with emergency lighting. Key control for operator, STOP, bell, overload signal with signaling to central control room or gatehouse. Cabin doors automatic. Electronic elevator switchboard, microprocessor. Elevator control by push buttons indoors, and outdoor control - call + send at each station. Elevator drive with smooth start (frequency converter).

The information provided represents only the minimum requirement for the lifting equipment. It is the CONTRACTOR 's obligation to adapt the technical parameters of the lifting equipment to the intended operation and purpose.

### Specific requirements for the design of individual building structures

Specific requirements for the execution of individual building structures are provided in Amendment D01.

## Requirements for machine technology, electrical equipment, SKŘ and related equipment

### Applicability of project documents

The initial conceptual design for the main wet desulfurization processes is provided in Amendment D01,  Supplement 1 to the CONTRACT.

This is a design developed in the preparatory stage of project documentation and represents one of the possible process technology solutions.

The binding obligation regarding the WORK is to comply with the technical conditions provided in this Supplement 1 to the CONTRACT and its amendments, the initial and restrictive conditions at the installation site (including the dimensional and height limitations of SOs where the equipment is to be installed) and other requirements specified in the CONTRACT.

While respecting this condition, the CONTRACTOR and its subcontractors have the full freedom to apply their best knowledge and engineering practice regarding the design and construction in terms of process technology and functionality and to offer to the PURCHASER the Best Available Techniques (BAT).

The CONTRACTOR designed solution must not reduce the usability, service life and operating characteristics of the existing process technology equipment.

### Common requirements for equipment of process systems and their subsystems

#### Back-up scope of machine components

Unless the required extent of backup is further specified in the requirements for the execution of the individual PSs and DPSs, the choice is the responsibility of the CONTRACTOR.

#### Requirements for main equipment

Note: “Lining” in the following text means any method of protecting the equipment from abrasion, erosion and negative chemical effects, while meeting the requirements of the PURCHASER.

Absorber

The design of the absorber shall ensure a uniform distribution of the absorption suspension throughout the cross-section of the absorber and prevent its overflowing under all possible operating conditions. At the same time, it is necessary to minimize sedimentation and deposition.

The absorber shall have a durable structure, reflecting the demanding corrosive and erosive environment with internal lining or protection by corrosion-resistant and abrasion-resistant material with a minimum chloride resistance of 20,000 ppm. The bottom of the absorber shall be sufficiently graded towards the drain. The gradient of the slope shall be determined by the CONTRACTOR.

In the flue gas inlet zone, where hot gas enters, refractory, corrosion and erosion resistant material is required.

In areas with high abrasion, such as an injection zone where the suspension is injected against the lining or protection, high-resistance material shall be used for lining or protection.

The CONTRACTOR shall prove by documentation or other evidence the suitability of the proposed material for lining or protection.

The equipment structure shall provide for a secure fastening of the suspended access systems (protective cages, gondolas, etc.) in order to ensure the possibility of concurrent inspection and maintenance work on the absorber in parts not accessible from the outside on gangways, if such inaccessible parts shall exist. The absorber sheathing shall be insulated within the meaning of requirement 4.3.2.10.

Absorber magazine (for limestone/gypsum system)

The absorber magazine, i.e. the lower part of the absorber, shall have a sufficient residence time to allow the dissolution of calcium carbonate, the oxidation of calcium sulfite and the formation of calcium sulfate crystals.

Oversaturation of the recirculating suspension in the absorber must be prevented.

A sufficient number of aerators or propeller atomizers and mixers shall ensure the uniform distribution of the components and solids in the suspension and oxygen input into the reaction throughout the operation time.

The aerators/propeller atomizers shall be fully resistant to the environment in the absorber and shall be made of abrasion and corrosion resistant material.

The injection holes for oxidizing air must be sufficiently dimensioned to prevent clogging.

The load-bearing structures of the absorber's internal fittings shall be sufficiently dimensioned and protected with respect to the required service life.

The design of the absorber must be such as to avoid damage by high temperature or flooding and to prevent material sticking.

The CONTRACTOR shall provide information on how to restart after an emergency shutdown.

The absorber magazine shall be positioned above ground level so that its contents can be completely emptied.

Droplet separator

Droplets carried by the flue gas stream shall be sufficiently removed by the droplet separator behind the absorption section. The maximum permissible droplet drift rate in the flue gas from the desulphurization stack is 50 mg/Nm3 R in all operating modes. The droplet separator shall be able to operate at least 12,000 hours before the pressure drop reaches the maximum value. An inspection manhole allowing inspection of the droplet separator condition shall be considered.

The droplet separator shall be of a proven type. The material used will be of reduced flammability. The segments shall have sufficient thickness and adequate strength to prevent damage during operation and manual cleaning during comprehensive repairs.

The droplet separator must be minimally two-stage (coarse and fine). Each stage must be equipped with a remote-controlled washing device on both sides. Checking its proper function must be enabled from the outside.

The droplet separators shall be constantly rinsed by process water.

Rinsing nozzles in droplet separator shall be designed to prevent clogging. Pipes and nozzles shall be constructed of durable material.

The droplet separator must be accessible from all sides without additional scaffolding for inspection during short stops.

During the planned shutdown, it is permissible to carry out manual cleaning of the droplet separator with water from the process water distribution system without using water pressure devices.

Flue gas ducts

The works on the flue gas ducts modification shall be carried out with the plant in operation in a period outside the heating season, the operation of boilers K4 and K5 is presumed (separate chimney inputs). For the flue gas ducts works, it shall be necessary to blind the inlets of the flue gas ducts of boilers K6 – K10 into the stack first. The blinding shall be carried out at the existing flange of the flue gas duct. Before the blinding, the flue gas duct shall be structurally secured (supported) in order to prevent the fall or collapse of its structure during the works execution. The detailed method of the blinding, flue gas duct modification and its reconnection to the stack shall be laid out in the DOCUMENTATION FOR EXECUTION OF THE PROJECT. The period in which the operation of the plant is limited to only two boilers (K4 and K5) shall not exceed 30 days and shall be stated by the CONTRACTOR in the schedule of works.

The flue gas duct connection design must meet the corrosion protection requirements (minimum length of shut down parts of the flue ducts, sealing by air).

Include suitable corrosion protection of the inner surface in the flue gas duct segments exposed to corrosive environment.

Thermal expansion of flue gas ducts must be allowed, but it is desirable that the number of flue gas duct compensators is as small as possible. If possible, the necessity of lateral compensation must be eliminated.

Flue gas condensate must return to the desulfurization process.

The flue gas ducts shall be designed for a maximum flue gas speed of 20 m/s.

The flue gas ducts shall be designed with a minimum wall thickness of 6 mm.

Internal reinforcement must not be used. If internal lining is used, the inner surfaces must be suitably adapted for its application. The external reinforcements and construction design of the flue duct corners shall be such as to prevent cracks in the lining.

Within the scope of WORK, the CONTRACTOR shall propose protection against corrosion  for both raw and treated flue gas ducts.

For closures and compensators, the CONTRACTOR shall provide information including the manufacturer's name, relevant technical data, the overall composition and a construction drawing.

The CONTRACTOR shall specify in the design the construction material for closures, frames, seals, etc. Only such closures and compensators with verified use in desulfurization operation shall be supplied. In the event of equipment repair it must be possible to mechanically secure the inlet and outlet closures in the closed position.

The elevation and position of the flue gas duct shall be designed with respect to the passive protection of the booster fan from flooding.

The stack shall be designed in accordance with the dispersion study (see Amendment D02).

Flue gas duct flaps

All flaps (of flue gas ducts) must be suitable for operation and use on flue gas duct with regard to the anticipated flue gas composition.

Shut-off flaps in the flue gas ducts (besides the existing flaps before and behind the fabric filters) shall be sealed by heated compressed air where necessary. The following configuration may be used for the closures:

two blowers, each with an output of 100%, for one closure,

two blowers (one in operation and one backup), each with a double power output for two closures, if this solution is acceptable from a process and safety point of view.

The flap seal can also be designed also by using air from PURCHASER´S air distribution system.

Sealing air blowers and associated fittings shall be controlled from the boiler control systems.

Fabric filter

The fabric filter shall be supplied with at least four filter chambers. Each chamber must be capable of separate shut down.

The filtration area shall be designed for flue gas quantity corresponding to all boiler operating points. In case of a failure (deactivation) of one chambers from operation, the remaining chambers (7 chambers) shall handle flue gas flow rate of up to 170,000 Nm3/h.

The difference between the inlet and outlet pressure shall be measured on the fabric filter, and the captured fly ash shall be shaken off from the hoses when the prescribed value is reached.

The shake off shall be automatic and shall be performed by a pulse of compressed air.

From the chutes, fly ash shall be transported by existing pneumatic transport to the existing dry ash silos of the individual boilers. The fabric filter shall be insulated and at least the chutes and the walls shall be heated so that the dew point of the flue gas is not reached.

At the filter flue gas outlet, the measurement of TZL concentration in flue gas shall be installed so as to immediately detect possible failures of the filter hoses. This measurement and signaling must be directed to the boiler control systems and concurrently it will serve as the dry stack emission measurement.

The delivery of the fabric filter must also include upgrading of the inlet and outlet flaps of the filters.

The fabric of the filter must meet the technical parameters for use in wet desulfurization technology.

#### Vessels, magazines, exchangers

- The equipment must be configured to allow easy operation and maintenance using common tools and devices for:

Access for internal inspections, repairs and cleaning (hatchways, inspection holes, internal ladders).

External access (optional service platforms, ladders, etc.).

Installation, lifting, disassembly, transport.

Storage structures and anchoring and the possibility of replacing possible internal filling and repair of the installation.

Insulation attachments.

Safety (safety valves, silo explosion vents, etc.).

Remote and local measurement and regulation (including local instruments, gauges).

Overflows.

Venting and draining.

Grounding.

Testing.

Marking.

Small orifice reinforcement.

Installation of construction inserts.

Disassembly of lids and heads (mounting arms, hinges, etc.).

Anchoring (bolts, nuts, concrete foundation anchoring).

Coating.

Protection against corrosion.

Cleaning.

- This equipment must further meet the following requirements:

Non-pressurized containers and magazines for hazardous media must be designed for minimum overpressure of 6 bar.

All these devices must be equipped with the prescribed safety features (safety valves, explosion vent tear membranes, etc.).

All these devices must allow emptying and be grounded.

Ventilation of vessels through detonation arrestors or similar equipment must be made and installed so that water or condensed media cannot freeze in this equipment.

Bulk material magazines must be equipped with aeration equipment and filter equipment with automatic regeneration to ensure that TZL concentration is not higher than 30 mg/m3 in the air emitted from the magazine.

- The CONTRACTOR shall be responsible for the correct function of the filling, aeration, material removal and filtration equipment of the existing lime and limestone silos.

Bulk material magazines, where there is a possibility that the dew point of the gases inside the vessel is reached as a result of cooling, must be insulated and heated.

The drain holes closures of containers storing hazardous media must be doubled.

All tanks and magazines must be equipped with inspection hole hatch doors with own rotating support structure. This applies to all hatches and inspection holes, not only on tanks and magazines.

Suspension tanks must be equipped with flushing nozzles placed at the mixer locations.

The usable volume of tanks, sumps and the sizing of the process technology must meet the requirements for the safe operation of the respective equipment and the requirements for handling emergency operating conditions.

#### Fans

The fans shall be designed and shall include:

Sound and thermal insulation.

Components for flexible mounting.

The flow rate and the total fan pressure must meet the specified conditions with a reserve, the ID fan and the oxidizing air blowers must have a reserve minimum 5% above the nominal value.

Fans included in the flue gas line or otherwise influencing the technological process must be equipped with remote power control via frequency converters.

The operating range shall be consistent with optimal efficiency.

Fans are required to be air-cooled, complete with standard accessories.

The fan design must allow easy maintenance and control by the operator.

The fan is required to operate with minimal vibrations and noise throughout the control range. If necessary, the fans shall be equipped with ventilated sound dampening hoods.

The fan motors must be designed so that the motor power reserve is at least 15% of the power required for the fan operating point (s), at the same time it must be able to cover the reserves in the flow rate and delivery elevation.

The final design of each fan, blower, and compressed air source of a process device is subject to PURCHASER’S approval, who will also assess the submitted documents for machine dimensioning and design calculation.

Requirements related to diagnostics:

All fans shall be equipped with measuring devices for bearing temperatures and motor winding temperatures, signaling of control elements position and signaling of important machine operating parameters such as pressure in the oil system, etc.

All rotating components, in particular motors, fans, compressors, gearboxes, etc. with a power output of more than 25 kW, shall be equipped with vibration monitoring.

These values ​​shall be introduced into the control system in accordance with chapter 6.2.

#### Pumps

Pumps shall be designed and shall include:

Process pumps shall have appropriate mechanical seals compatible with process media and operating conditions, sealing materials shall be chosen so that more durable material shall always be used if more options are available.

The operating point of the pump within the control range of the technology must not be near an unstable part of the characteristic (surge area).

A standard power reserve of minimum 10% above the power corresponding to the pump design point (s) is required.

Pump motors must be designed so that the engine power has a reserve of at least 15% of the power required for the pump operating point (s).

The design shall reflect the influence of the changing resistance characteristic of the process technology due to long-term operation.

The pump design point shall correspond to the best efficiency range.

Installed backup or replacement pumps shall be designed to avoid a reduction in the performance or efficiency of the relevant process section in all operating modes, unless otherwise specified.

In pumps whose failure would result in operation limitations or an equipment shutdown, at least one pump must be installed as a stand-by capable to replace the pump in operation. This does not apply to recirculation pumps.

Pumps where a flow rate restriction could result in an impermissible overheating of the pumped liquid must be equipped with a minimum bypass.

Suspension pumps must allow flushing and the penetration of abrasive particles into the seal and sealing surface must be prevented.

The active and exposed parts of the suspension pumps shall not be rubberized, but shall be made of stainless material that resists the corrosive and abrasive effects of the suspension. Other solutions, such as silicon carbide protection, are allowed in justified cases; the selection must be substantiated by the CONTRACTOR and authorized by the PURCHASER.

It must be optional which pump will work as backup and which one as operational. This does not apply to recirculation pumps.

Automatic start of the backup pump is required in the event of a failure, malfunction of the operational pump, or when the flow rate drops below a predetermined value.

A pressure gauge shall be placed before and after each pump, and where flooding and deaeration  of the pumps will be required, this deaeration and flooding shall be automatic.

Piping next to the pumps shall be equipped with spacer rings so that the pump is easily removable.

Pump alignment after installation must be documented by a protocol approved by the PURCHASER.

The pump service life is similar to that of fans. This does not apply to suspension pumps; here minimum operating time of 1 year without changing worn parts is required.

The suction piping of large circulation pumps must be designed so that the flow velocity profile of the fluid in suction is not shifted to one side (sufficient suction length for stabilizing after bend).

The pumps must be protected for the event of a discharge shut-off by a safety valve which is not a part of the pump.

All pumps must be designed to withstand the pressure generated during operation when the discharge valve is fully closed. The noise level must comply with the requirements specified in this documentation.

The pumps must withstand maximum possible reverse rotation speed when reverse flow occurs with respect to the delivery height and the flow rate.

The documentation for the design of all pumps as well as the design calculation of all pumps shall be submitted to the PURCHASER and shall be subject for approval in the design stage.

Requirements related to diagnostics:

All pumps shall be equipped with measurement devices for vibration, bearing temperatures and motor winding temperatures.

All rotating components, in particular motors, fans, compressors, gearboxes, etc. with a power output of more than 25 kW, shall be equipped with vibration monitoring.

These values ​​shall be introduced into the control system in accordance with chapter 6.2.

#### Mixers

Mixers shall be used for all sumps and tanks where the suspension is gathered or where media capable of gravity stratification is gathered.

The mixers and their drives shall be equipped with devices preventing overload from a viscosity increase in the mixed media. In the event of such intervention, it is necessary to ensure safe shutdown of the technology i.e. removal of the suspension.

The mixers shall be made of stainless steel (unless the properties of the mixed material exclude this).

The mixer must be capable of stirring the mixed medium even after 12 hours of stopped operation.

The mechanical seal of the pump shall be replaceable from the outside when operating the respective reservoir or tank.

For the service life of the mixers, conditions similar to those for fans apply.

All mixer components shall be equipped with vibration monitoring data transmitted to ŘS in accordance with chapter 6.2.

#### Drives

Where not stated otherwise in this Supplement 1 to the CONTRACT, all drives shall be electrical. Their type will be suitable for continuous operation, with the exception of electrical motors for shut-off fittings, which will be designed for short-term operation.

The motors shall be able to start with at least 3 cold starts and 2 hot starts within 1 hour and 7 cold starts and 4 hot starts within 24 hours.

Electrical motors with a power output of more than 25 kW shall be controlled by frequency converters, with the exception of electrical motors of recirculation pumps.

Electrical motors with a power output of more than 50 kW shall be equipped with an operating hour counter.

Electrical motors with a power output greater than 75 kW shall be equipped with a thermal protection in the winding.

Electrical motors controlled by frequency converters shall be equipped for operation with frequency converters (thermal protection in windings, external cooling, electrical insulation of bearings, etc.).

Reliability and the number of electrical motor operation hours without maintenance must be consistent with the maintenance and inspection periods of the driven machinery.

Other types of drives (e.g. pneumatic) are only allowed in justified cases; the selection must be justified by the CONTRACTOR and must be approved by the PURCHASER.

#### Pipes, fittings and accessories

Requirements and standards

Similar rules that apply to machinery and equipment also apply for pipes, fittings and accessories. The design of the piping, connection dimensions and the adjustment of the flange sealing surfaces must comply with the Czech standards (ČSN 13 0020, ČSN EN 13480-1 ÷ 6, ČSN 130072 and following).

Pipes and flanges requiring for service life and correct operation a defined position shall be provided with a lock (position definition).

Layout

The layout of the piping must be in accordance with the general rules and best engineering practice and experience of the CONTRACTOR. Easy handling and maintenance must be respected. Pipes must be with minimal vibrations. The forces and moments transmitted by piping to the equipment and machinery connections must not exceed the forces and moments allowed by the equipment supplier. Pipes must be labeled according to the media used - paint color, stripe colors, labels and arrows).

For nominal pipe diameters see ČSN EN ISO 6708 (DN 15, 25, 40, 50, 80, 100, 150, 200, etc.).

Pipes and accessories

Pipes including accessories must meet all strength and dimensional requirements and conditions for the construction of all pipelines and routes considered.

Pipeline supply must include all pipelines within the WORK scope within the specified supply boundaries. Pipelines shall be subjected to the prescribed tests (pressure, sealing, etc., and supported by certificates) after mechanical completion.

Piping supports and hinges must be made according to ČSN. Hinges and supports for cold distribution piping must have thermal insulating inserts.

All pipelines, including equipment, must be conductively interconnected throughout the pipe lengths and properly grounded.

Pipes must be installed entirely in a gradient and the content must be releasable; piping must be provided with air venting and release valves.

Piping systems of all media must be fitted with stop valves to allow maintenance work during operation.

The suspension transport pipeline shall be designed for a speed of 1.5 - 3 m/s. This pipe must be flushable and stable accessories must be installed to enable flushing.

The pipes must be designed for the least favorable conditions they may be exposed to. Consideration must also be given to the conditions arising when commissioning the equipment and its cleaning.

Pipes subject to vacuum must be designed for complete vacuum.

Piping systems for hot water, fire water and condensate must be subjected to an analysis of pressure surge risk  prior to installation.

The piping for the distribution of dry compressed air shall be made of stainless steel.

Appropriate particle separators or self-cleaning permanent particle filters must be installed in the intake manifold for all pumps, separators or filters and must be separated by shut-off fittings with a bypass.

Piping routes must be designed to avoid any pressure shocks in pipes.

Connection seals disassembled during tests (pressure test, etc.) must be replaced after the test.

The use of threaded connections for process pipelines is prohibited.

Compressor discharge pipes must include a return and shut-off fitting for each compressor.

The CONTRACTOR shall ensure that all piping is capable of continuous and reliable operation. Conditions in piping leading to its failure or shortening of its service life are inadmissible.

- The following shall be considered as inadmissible:

Leaks of all kinds on piping, pipe fittings, fittings, pumps and compensators.

Detachment of piping from support, hinge or guide.

Lifting of the pipeline over support.

Pipeline misalignment from support.

Floating pipeline routes without fixed points.

Pipe vibration induced by the dynamic effect of flowing media.

Freezing of pipes, tanks, venting and drainage fittings.

Inability to completely drain and de-aerate the piping systems.

Water ingress into the insulation.

Device corrosion.

Pipe aeration or evaporation of water in pipes due to low pressure.

Water column separation or other water shock impacts on piping in the event of a pump failure or hydrodynamic shock from a changing fitting position.

- Piping routes shall be designed with regard to thermal expansion of the pipeline so that the permissible forces and moments on the individual devices are not exceeded

Fittings

All fittings necessary for the proposed level of automated operation shall be equipped with servo-drives.

New equipment shall be fitted with such number of fittings so as to ensure safe separation from the existing installed equipment. The fittings shall be accessible for both inspection and repair.

Fitting actuation must not cause pressure surges in the pipeline.

Manual shut-off fittings from DN 150 and larger must be fitted with gearboxes.

For media with a requirement to prevent leakage to the environment, fittings using rising spindle shall not be used. If a fitting with a rising spindle is used, then use a fitting with bellows.

For water and condensate, ball valves or possibly flaps shall be used.

All control fittings shall be 100% backed up. If a control fitting fails, it will be possible to repair and replace it without interrupting the operation of the process technology.

The design base for the dimensioning of all control fittings, as well as the dimensioning calculations for all control valves, shall be submitted to the PURCHASER in the design phase.

Other

All the process technological elements (valves, servo drives, sensors) shall be permanently accessible, also from any potential service platforms.

#### Construction material and indoor anti-corrosion protection

General requirements and standards

The quality of the material must meet the requirements of the mechanical design according to the design calculation parameters and at the same time must be fully compatible with the relevant media, operating parameters and other conditions influencing material selection. The corrosion-resistant, abrasion-resistant, or possibly refractory and heat stable material must be optimum and selected according to the latest standards and experience.

The CONTRACTOR shall be responsible for the selection of the material, but the quality of the material for pressure vessels, pipes, etc. must also meet the requirements of the relevant Czech standards.

The CONTRACTOR shall design and implement access to surfaces with corrosion-resistant treatment to inspect the status of  the anticorrosive treatment.

In the design, the CONTRACTOR shall specify the quality of the material and the standards for each equipment item, pipe system, etc., and must justify the material selection (comparison of suitable alternatives) for the following items:

flue gas duct lining material;

absorber lining  (protection) material;

unlined metallic materials in flue gas ducts and absorbers;

flue gas duct drainage system;

suspension pumps;

piping and fittings for suspension.

The CONTRACTOR  shall specify the list of materials used by quoting the standard, composition and main characteristics as well as the Czech equivalents.

Corrosion allowances

The corrosion allowance shall be determined by CONTRACTOR based on long-term experience from the operation of existing equipment.

The corrosion allowances shall be specified for each material group used for equipment, piping systems, etc.

Internal corrosion protection

Where necessary, internal corrosion protection, based on the experience of the CONTRACTOR, the special nature of construction and character of the equipment, as verified by long-term operation, shall be used. As with material and corrosion allowance, internal corrosion protection and its application are fully the responsibility of the CONTRACTOR and under its warranties.

In the DESIGN, anticorrosive protection must be stated for each device where it is used by the CONTRACTOR. This will include the technological process of removing corrosion products from affected existing surfaces.

The CONTRACTOR shall specify the information on the use, reliability and suitability of the proposed corrosion protection, referring to the equipment for which it is in suitable for  long-term operation, the name of the manufacturer and its experience. Also stated will be the specifications for required repairs, repair procedures, their frequency, time requirements and service life.

In the design, the CONTRACTOR shall submit a specification sheet with qualitative and quantitative data on the chemical composition and physical and mechanical properties of the corrosion protection agent to be used.

- Basic requirements for equipment surfaces to be provided with lining:

Construction inserts must be excluded except when necessary for process technology reasons

Dimensioning of wall thickness and number of external reinforcements shall ensure that deformations due to operating conditions and necessary inspection walks are not greater than 5 mm

The diameter of the throats must be minimum 80 mm

All areas to be lined must be visible and easily accessible

An even and smooth surface without sharp corners and edges is an indispensable condition for the corrosion protection of the entire surface. The surface of the components must not have dents such as from welding, pores and defects. Area of grinding when removing the defect must be sufficiently large.

#### Insulation

These requirements apply to the thermal insulation of pipes, tanks, fittings and other assembled parts.

They represent the basic description of the thermal insulation and do not relieve the CONTRACTOR of its obligation to install faultless thermal insulation according to the state of the art, even if no details are provided hereinbelow.

All components whose operating surface temperature exceeds 50 °C shall be fitted with a thermal insulation layer (or other safety measure to prevent injury from touching hot surfaces). All operating conditions and all climatic conditions must be taken into account.

Excluded from this are the technically conditioned thermal bridges and parts of installations where not negatively impacting other components or not subject to any safety regulations or economic aspects (flue gas scrubber etc.). Cold and warm bridges are to be avoided.

Insulation surface temperature shall be maximum 50 °C; if this could not be achieved in unique cases, these surfaces must be protected from contact with persons.

Insulation of hot water pipelines and tanks should be dimensioned in a way that heat losses by radiation, regarding energy efficiency and economy, are not exceeded. Insulation of pipes, absorber and tanks with cold water should safely prevent moisture condensation when the lowest temperatures are considered.

Plastic pipes need not be insulated to prevent moisture condensation unless the insulation is required for energy efficiency economy.

Only perfect insulating materials with known thermal insulating properties and guaranteeing compliance with the above criteria shall be used.

The insulation material must be dry before and during installation. It must not have negative or destructive effect on the insulated piece of equipment, e.g. due to unacceptably strong corrosion, moisture excretion, electrolytic corrosion, and similar.

All insulated surfaces must be clean and dry prior to the installation of the insulating material. Fundamentally, wet or icy surfaces cannot be insulated.

Insulation materials must not burn or sinter at the occurring temperatures. Thermal insulation must not be detached from the insulated part of the equipment, it shall not sag in horizontal position and settle in vertical position. The thermal expansion of the insulated part of equipment is to be compensated, if necessary, by means of telescopically arranged casing rings, or by a correspondingly larger prestressing. By prestressing, the occurrence of hollow spaces between the individual insulation sections at full elongation must be avoided.

- The insulating material must be completely free of impurities and iron particles, must not in any way compromise the material of the insulated item and must have the following characteristics:

Chemically inert, sulfur-free, asbestos-free, free of alkaline water-soluble constituents, resistant to rotting, hot water and water vapor, even when alkaline, and absolutely non-flammable.

The best approach is to install the insulation in two or more layers to the required total thickness. The joints of the individual layers of insulation should not be stacked to ensure that the thermal bridges in the joints are interrupted. Insulation should always be protected from weather impacts.

When the insulation thickness is greater than 120 mm, the insulation is installed in at least two layers with layers overlapping in the joints.

Insulation and sheathing should be installed so as to allow piping dilatation without damage. Pairs of flanges and compensators shall be fitted with removable lids.

Insulation material for stainless steel piping must not contain chlorides (the material must be certified for stainless steel pipe insulation). Stainless steel surfaces can only be cleaned by stainless steel brushes. Impurities must not be removed using solvents or detergents containing chlorides.

Fittings of all sizes, flanges and places requiring access for operation and maintenance shall be fitted with removable insulating sleeves.

Supports and hinges shall be fitted with insulating inserts, especially for insulation preventing cold loss.

For vertical piping, the insulation shall be secured by retaining and binding wire to ensure tight fitting to the pipe. To prevent the insulation mats from settling or sliding off, their weight is to be borne by supporting rings.

It is important that the surface of the pipeline and equipment on which the insulation is installed is  properly treated. Surfaces consisting of unfinished steel must be stripped of dirt and rust by grinding. Grease can be removed with detergents or solvents.

There must be sufficient free space between the insulated pipes (for installation and adjustment of the insulation).

Taps, valves and sliders should be positioned so that they can be operated without standing on the insulated pipeline.

The valve spindles should not be installed upwards to prevent water from entering the insulating material.

For venting, drainage and exhaust pipes in the vicinity of ​​platforms, stairs and service platforms, protective thermal insulation is required to protect operating personnel.

When the equipment noise level exceeds 85 dB (A) or the limits prescribed by sanitary regulations for the given operation, appropriate sound insulation shall be installed on the equipment.

Heat insulation of flue gas ducts and heating, ventilation and air-conditioning systems performs the function of fire protection, sound protection and protection against condensation. Insulation of air-conditioning pipelines is attached to the outside of the pipeline by means of an adhesive or welded pins made of steel or aluminum, or the pipe insulation is fastened with straps. For aesthetic reasons, the joints of insulation boards or mats are covered by adhesive aluminum strips. All joints should be tight and sealed with adhesive tape. If necessary, cladding shall be mounted on the insulation. At the same time, the optimum performance parameters of the insulated equipment must be maintained.

#### Sheathing, support structures

The insulation sheathing shall consist of a smooth metal sheet (AlMn semi-hard, DIN 1725), purely circular in the form of a sheath and mounted on spacers. It is installed by passivated or stainless steel screws in the longitudinal seams. The distance between the screws must not be greater than 200 mm.

For horizontal pipelines, longitudinal seams are made on the bottom side. Circular seams of individual metal sheet contacts shall be hemmed.

The offset of the longitudinal and circular seams shall be dimensioned in such a way that no water droplets or leakage water can penetrate and moisture penetration is fully excluded. In addition, the offset on the ring seams should be adjusted so that the sheet metal can withstand the heat expansion and pipeline dislocation without damage.

For outdoor sheathing, the bottom should be configured to allow dripping.

Plastic may also be used, if necessary, for sheathing, provided its parameters match the conditions where used.

No water droplets or splashes should penetrate into the sealing through sheathing joints.

To attach the sheathing, stainless steel screws for sheet metal, min. 4.8 x 13 mm, quality A2 shall be used. The distance between the screws must not exceed 200 mm.

Sheathing holes for hinges, supports, etc. must be hemmed.

Type of sheathing:

indoor: aluminum sheet (smooth)

outdoor: painted aluminum sheet.

The following sheet thickness shall be used:

Sheet 0.8 mm for sheathing up to DN 100.

Sheet 1.0 mm for sheathing above DN 100 and for flange cabinets and valve covers.

Support structures, spacers

When using insulating mats, spacers are fundamentally required from DN 100 inclusive, or possibly from insulation thickness 60 mm inclusive, with spacing of not less than 950 mm to ensure a uniform insulating thickness and circular shape of the sheathing.

Vertical standing vessels and piping shall be fitted with clamping rings with spacing of maximum 2.0 m to prevent settlement of the thermal insulation. The heat insulation can also be installed from the pipe holders; then it is to be placed on "S" hooks at an appropriate spacing and provided with sufficient sliding seams.

The outer and inner clamping rings of the spacers are generally fastened by means of screws. Only screw connections from M6, inclusive  are permitted. Binding wire, etc., must not be used.

Care must be taken to ensure that these spacing structures do not form thermal bridges and do not cause additional thermal losses. At a 400 °C pipe temperature, principally discontinuous flat steel spacer inserts are used. Joints are separated by IT inserts. The part which comes into contact with the pipe is made of heat-resistant steel. Also the clamps attached to the tube in this temperature range.

Welding of any kind is fundamentally forbidden on insulating components!

However, if it is unavoidable to weld the supporting structures to the components, it may be done only by the CONTRACTOR upon an agreement with the PURCHASER.

When installing insulation, the principles of work safety and environmental protection must be observed.

#### Surafce treatment and coating

General

Corrosion protection shall be applied to all carbon steel components included within the scope of CONTRACTOR´S delivery and shall consist of a primer, interlayer and top coat. The complete primer, interlayer and top coat is carried out at the manufacturer's plant. Standard machines and equipment such as pumps, fittings, etc. shall also be delivered with a surface finish. When installing and commissioning, appropriate protection measures must be taken (only repairs of damaged surfaces shall be carried out). The coatings must withstand the level aggressiveness of the given environment and service life requirements of the equipment.

It is not allowed to use environmentally harmful materials in coating.

The design of the coating systems shall be governed in particular by ČSN EN ISO 9223.

The required coating life is 10 years, and this requirement shall drive the selection of paint systems, to be documented by paint system vendor certificates.

The paint system must be specified by the CONTRACTOR in advance in the design and must be approved by the PURCHASER before application.

Color solution for the machinery and equipment paintwork shall be subject to PURCHASER’S approval and the pipe color design shall conform to ČSN 13 0072 and shall also be subject to PURCHASER’S approval.

When PP, PE, galvanized steel, stainless steel and insulated pipes are used, the color paint shall be replaced by colored stripes.

The coating of all surfaces to be protected must comply at least with the following structure:

| Clean sand blasted metal | min. Sa 2.5 |  |
| --- | --- | --- |
|  | Minimum thickness of dry film [µm] | Mean thickness of dry film [µm] [µm] |
| First primer Second primer | 30 30 | 60 60 |
| Interlayer Top coat | 30 30 | 60 60 |
| Total | 120 | 240 |

The minimum thicknesses of the layers (dry film thickness) must not be less than the set value at any single location.

The color shade of standard equipment such as valves, tools, etc. may be applied according to the CONTRACTOR´S standard; regarding other equipment (pumps, motors, gear motors, mixers, compressors, etc.) the CONTRACTOR shall conform to the CUSTOMER'S color concept. Base coats, interlayers and top coats must be compatible and overcoatable.

On insulated flue gas ducts only two heat-resistant coatings shall be applied, each with a minimum thickness of 30 μm. Also, on the other devices on the flue gas ducts, at least two heat-resistant base coats shall be applied, each with a minimum thickness of 30 μm.

The CONTRACTOR is responsible for the professional selection and flawless quality of the coating system.

Corrosion protection work must be carried out with great care and expertise.

Preliminary surface treatment for primer

Surfaces must be thoroughly pre-treated and abraded by sandblasting.

Sandblasting according to SIS 05 59 00 (Svensk Standard) SIS/1988, (ISO 8501-1: 1988), quality class Sa 2.5 (performed at the manufacturing plant).

All splashes after welding, slag after welding or burning, chips, etc. must be completely removed. Also, all steel rolling errors (duplication) must also be eliminated by grinding.

Welds must be welded impermeably. Seam welds are not permitted. Sharp edges must be chamfered.

Priming

The first primer must be applied as soon as possible while preventing moisture access, at least within 6 hours, at the latest on the same day as sandblasting.

Both primers shall be applied in different color shades.

Both first and second primary coats must be based on unmixed two-component resin (without additional fillers).

If the coating is exposed to temperatures above 80 °C, a zinc-silicate coating must be used for the priming.

Interlayer and top coat (overcoat)

As an interlayer, an iron/mica based paint based on a two component resin must be used.

For top coats in indoor or outdoor areas, binders based on two component polyurethane are to be used.

On-site repair work

Damaged primer, interlayer and potentially the topcoat must be repaired on-site as follows:

Carefully grind the transitions and completely remove rust.

Apply primer with min. 60 μm (2 coats).

Apply top coat min. 60 μm (2 coats).

Interlayers and top coats should be applied in accordance with the quality of the original paint.

Weather conditions during corrosion protection work

During the corrosion protection work and during the corresponding drying time of the interlayer and top coat, minimum 4 °C difference between surface temperature and air dew point is required. The CONTRACTOR is obliged to comply with this requirement.

#### Winter measures

The WORK and its individual SOs/IOs/PSs must be designed and constructed in such manner that no  failures caused by freezing shall occur in the winter period. These include, but are not limited to heating and suitable layout of condensate drainage, welded-on drainage and venting components, air release/intake fittings, condensate drains from safety valves, etc.

When using electrical heating cables, self-regulating cables are preferred.

### Specific requirement for the design of individual process PSs/DPSs

The specific requirements for the design of the individual technological units are provided in Amendment D01.

### Electrical part

The desulfurization process technology shall be powered from the new 6kV substation. This substation shall have 2 supply connections from the existing reserve switchbays of the R6KYII substation. Within the work scope, these switchbays shall be adapted to power the new 6kV switchboard and shall be equipped with short-circuit current reduction reactors.

Recirculation pumps and the booster fan supplied within the work scope shall be powered from the modified reserve switchbays of the existing 6kV substations R6KTI and R6KYI.

The equipment supplemented to the existing operations of the Limestone Handling and the Mixing Center/Agglomeration (switchboards) shall be added to the R04KYI (00BFA) 66A/B substation (behind limestone silos) at voltage 0.4 kV. The existing substation is assumed to have sufficient space and power reserves to power the newly installed equipment. If this reserve is not sufficient, a new switchboard shall be provided by the CONTRACTOR.

The current layout of electrical equipment is shown on single-ended diagrams (see Amendment D05).

The power rating of individual devices shall be determined by the CONTRACTOR according to the technology used.

#### Basic requirements

All electrical equipment shall be power supplied from the 0.4kV or 6kV system.

Equipment Reliability

The electrical equipment must be designed so that the temporary loss of voltage of its own consumption, short-term loss of control voltage 24 V, 230 V, circuit breaker failure, measurement/transducer failure do not cause the new desulfurization technology to shut down. These outages shall be signaled by the control system.

Equipment safety

The electrical equipment must be designed so that the process equipment can be safely shut down with a permanent loss of power for own consumption.

External influences

The protocol on determination of external influences shall be prepared by the contractor in accordance with ČSN 33 2000-5-51 ed.3.

Distribution systems

NN system, nominal voltage of own consumption substations:

3PE AC 50Hz 6kV/IT

NN system:

3PEN AC 50Hz 400/230 V/TN-C, TN-C-S

3NPE AC 50Hz 400/230 V/TN-S

2-220V DC / IT

Secondary circuits of instrument current transformers: 5 (1) A / 50 Hz.

ASŘTP (Automated System of Technological Process Control) power supply

1NPE AC 50Hz 230 V/TN-S

Protection against electric shock

Protection against dangerous contact with parts not under voltage shall be carried out in accordance with ČSN EN 61140 ed.3, ČSN EN 61936, ČSN EN 50522 and ČSN 332000-4-41 ed.3.

System 3 AC 50Hz 6kV/IT:

Measures according to ČSN EN 61936-1 art. 7, 8 and 9.

System 3PEN AC 50Hz 400/230 V/TN-C, TN-C-S:

Automatic disconnection from the source according to ČSN 33 2000-4-41 ed.3, article 411.

System 3NPE AC 50Hz 400/230 V/TN-S:

Automatic disconnection from the source according to ČSN 33 2000-4-41 ed.3, article 411.

System 1NPE AC 50Hz 230V/TN-S:

Automatic disconnection from the source according to ČSN 33 2000-4-41 ed.3, article 411.

System 2-220V / IT:

Automatic disconnection from the source according to ČSN 33 2000-4-41 ed.3, article 411.

Electromagnetic Compatibility (EMC)

EMC shall be designed in accordance with valid ČSN, EN standards. Limiting interference in the surroundings shall be ensured by adhering to the equipment manufacturer's recommended installation, using shielded power cables to motors powered by converter, separation of control and power cables using spacers, partitions or separate routes, with restriction on parallel position of  power and signal cables. Adverse back effects of frequency converters on the power supply system shall be prevented by using input filters.

Protection of electrical devices against overcurrents in NN networks

The design shall follow ČSN 33 2000-4-43 ed.2 so that the individual elements of the equipment are protected against exceeding the limit values ​​for the protected equipment operation. This protection shall be provided by protective elements (circuit breakers, fuses, thermal relays) protecting directly the electrical equipment when the set limit is exceeded.

Protection of electrical devices against overcurrents in VN networks

The design shall follow ČSN 33 3051 so that the individual elements of the equipment are protected against exceeding the limit values ​​of the protected equipment operation. This protection shall be provided by electrical protective elements, which in conjunction with the respective switches shall protect directly the electrical equipment when the set limit is exceeded.

Protection of electrical devices against overcurrents in VN systems

Protection against electric shock shall be carried out in accordance with applicable regulations and standards, in particular ČSN 33 2000-4-41 ed. 3, ČSN EN 61140 ed. 2, ČSN EN 50 522, ČSN EN 61 936-1 and all related standards.

Voltage sags, automatic backup and selectivity

The voltage sags shall comply with the requirements of ČSN 34 1610 and ČSN 38 1120. In the event of a voltage failure on one of the connections for the new desulfurization vn switchboard, the automatic backups shall be designed so that the second connection is not overloaded and then also switched off. The type of automatic backups shall be unified with the existing own power consumption switchboards. The protections on output switches of the new desulfurization vn switchboard shall be fully selective with protection on the supply switchbays as well as the output switches of the upstream substations. In case of a malfunction, only the affected part shall be turned off.

Level of supply importance

Appliances shall be divided into three categories according to the valid standards ČSN 34 1610 and ČSN 38 1120 into three categories.

The main switchboard 6kV and main NN switchboards provide power supply No. 2. These switchboards have two independent inputs, automatic backup and the load on the VN/NN transformers shall be maximum of 100% of their nominal output even in an outage and while taking over the load of the backed up transformer. The switchboards will be single-system.

Secondary switchboards power supplied by two independent connections are included in power supply No.  2.

The switchboards with one connection are included in power supply No 3.

Reactive power compensation

Reactive power compensation shall not be implemented.

#### Description of connections

The new 6kV desulfurization switchboard shall be connected to two existing 6kV substation backup switchbays, so as the circulating pumps and a combustion air booster fan. The supply switchbays to the new 6kV switchboard shall be implemented with mutual automatic backup. Appliances supplemented to the limestone suspension production technology shall be connected to the existing nn substation 00BFA.

Within the scope of the work two VN/LN transformers shall be supplied, connected to the new vn switchboard. One of the transformers shall power the newly supplied process technology, the second transformer shall be primarily used to power the wiring system in buildings. Both transformers shall have the same parameters so that, in the event of a process transformer failure, the transformer, which is primarily intended for powering the building wiring, shall be able to supply the desulfurization process technology.

In the event of power loss, replacement power sources shall be installed within the work scope. A diesel generator to power the flue gas cooling pump and suspension mixer shall be supplied and connected. The power output of the diesel generator shall be determined by the contractor based on the requirements of the supplied technology.

Appliances supplemented to the limestone suspension technology shall be connected to the existing 00BFA switchboard if this switchboard has sufficient space and power reserves. Otherwise, a new nn switchboard shall be supplied by the contractor within the WORK scope.

#### Layout  solution

The said 6kV substations are located in the HVB building (+0.20m), room 1.27. The 0.4kV R04KYI substation is also in the HVB building (+0.20 m), room 1.45.

All new VN and main NN switchboards, VN/NN transformers, motor switchboards, building wiring switchboards, UPS and central emergency lighting unit shall be located in the newly constructed SO03 substation building.

The diesel generator shall be supplied and installed as a compact unit in a container, the container shall be located north of the SO03 substation.

#### 6kV substations

The existing switchbays of 6kV substations R6KYI, R6KYII are of the vault-type design. The R6KTI substation is of the cabinet design and is equipped with flash protection

The reconfigured 6 kV switchboard switchbays shall be implemented with a complete design of connections to the control system. Both switchbays shall be monitored and controlled by ŘS MicroSCADA as used in TKY.

The newly supplied switchboards shall be of a cabinet design, all the outputs shall be equipped by vacuum switches with slide-out carts.

The switchboards must comply with ČSN EN 62271-200 ed.2, it must have the prescribed protection from external environment and electrical equipment according to ČSN 33 2000-1 ed. 2 Low voltage electrical installations - Part 1: Basic principles, assessment of basic characteristics, definitions, definitions ČSN 33 2000-5-51 ed.3: Electrical equipment - Selection and erection of electrical equipment – Common rules, and related standards.

The switchboards shall be adapted for cable connection from the bottom.

The switchboards shall be equipped with the necessary PTP for measurement and protection.

The individual switchboard outputs shall be equipped with terminals for protection, measurement, control, diagnostics and monitoring. The terminals shall be connected via a communication line to the existing ŘS.

Flash protection shall be installed in all new 6kV switchbays, full compatibility with the current flash protection system is required.

| Parameter | Unit | Value |
| --- | --- | --- |
| Nominal voltage | kV | 7.2 |
| Busbar material | - | Cu |
| Switchgear manufactured according to standard | ČSN, IEC |  |
| Circuit breakers: |  |  |
| arc quenching type | - | vacuum |
| nominal voltage | V | 7.2 |

Instrumentation Current Transformers (PTP)

Current instrumentation current  transformers must comply with ČSN EN 61869-2.

PTP parameters such as their ratios, nominal load and other properties must conform to and be compatible with protection and measurement requirements.

PTPs shall comply at least in the following parameters:

| Parameter | Value |
| --- | --- |
| Nominal voltage | 6 kV |
| Insulation voltage | 7.2 kV |
| Nominal current secondary | 5 A |
| Nominal frequency | 50 Hz |
| Number of cores | 2 |
| Core type - Core I - accuracy grade - overcurrent number | 0.2 % < 5 |
| Core type - Core II - accuracy grade | 5 P10 |
| Short circuit current - short time (1 sec) - dynamic | as required as required |

#### Switchboards 0.4 kV

Switchboards 0.4 kV shall be implemented with a complete link solution to the control system. The modules shall be equipped with the ability to adjust blocking, sending diagnostic data, alarms and timestamp events, and interfaces to control and monitor the switchboards and their accessories.

The switchboards must comply with ČSN EN 62271-200 ed.2, must have the prescribed protection from external environment and electrical equipment according to ČSN 33 2000-1 ed. 2 Low voltage electrical installations - Part 1: Basic principles, assessment of basic characteristics, definitions, definitions ČSN 33 2000-5-51 ed.3: Electrical equipment - Selection and erection of electrical equipment – Common rules, and related standards.

The switchboards shall be adapted for cable connection from the bottom.

Links to the automated technological process control system  shall be implement by type.

The switchboards shall have a minimum 10-percent reserve in the number of each output type, at least one piece of each type.

Additionally, the switchboards shall have a 10% internal space reserve.

#### Electrical protections

All adjusted 6kV switchboard switchbays and all new 6kV switchboard switchbays shall incorporate new electrical protections.

The protection shall be carried out in accordance with the ČSN 33 3051 standard.

The electrical protection system error signaling shall be connected to the control system.

frequency converters

Frequency converters, if used, shall preferably be from one renowned manufacturer.

Converters powered from the  0.4kV grid shall preferably be in a 6 pulse configuration to eliminate higher harmonics and shall include a filter enabling compliance with ČSN EN 61000-6-2 ed.3 and ČSN EN 61000-6-4 ed.2 to EMC for industrial environments and other relevant applicable standards. It is assumed that the THDI current distortion of frequency converters for NN drives shall be 30% maximum.

The frequency converters must be made in accordance with ČSN  EN 61800 (set of standards).

The frequency converters must be capable of continuous operation with nominal parameters when the input voltage fluctuates on the primary side of the frequency converter within range ± 10% Un, and shall continue to operate at transient voltage fluctuations - 20% Un and at input frequency fluctuations between 46 to 53 Hz.

At motor start or in the event of a backup or in the event of a short-term power outage, the control shall be set so that the starting current from the power supply substation does not exceed 1.5 (one and a half) multiple of the nominal current.

The frequency converters must be capable of continuous operation even in the event of a short interruption of the supply voltage from the power substation for about 2 s.

The engine speed range control must meet the requirements for the powered drives. In the entire revolution range, the engine cooling must be maintained. Winding warming must not exceed permitted warming values ​​according to ČSN EN 60034-1 ed.2.

The power factor at the input of the frequency converter shall be at least 0.95.

The frequency converter shall have at least the following protection functions:

overcurrent,

short-circuit,

grounding,

loss of input and output phases,

overvoltage,

undervoltage,

high temperature,

motor overload,

motor blocking.

Filters to provide sinusoidal voltage and current for motors shall be installed on the output.

From the converter, these values shall be transmitted to ŘS and the FM control panel: three-phase motor current, motor voltage, motor active power and motor frequency.

The outputs for transmission to ŘS shall be analogue, at 4 ÷ 20 mA.

The frequency converters protection and operating temperature range shall correspond to their working environment, the PURCHASER prefers location of the converters in a separate substation.

The frequency converters must be vector-controlled and must handle flying starts as the rotors of the motors will rotate even when the electric motors are switched off, and also during short-term power outage and repeated restart of the electric motors, the rotors of the electric motors will always be at a non-zero revolution speed.

#### Diesel generator

A diesel generator (DG) shall be used to provide emergency power supply, its power output shall be designed by the CONTRACTOR according to the technology used and which during a power outage must be dimensioned to provide not only a safe shutdown of the equipment but also to keep in operation all process equipment required to prevent subsequent damage due to sedimentation, setting, pollution, etc.

The diesel generator shall have the following parameters: 3x400V AC, 50Hz, maximum voltage drop 10%, maximum frequency drop 5%, maximum THD 10%, maximum take-over time of the first load from DG start must ensure safe backup and subsequent shutdown of the technology.

The power output shall be determined by the contractor according to the power consumption of all the appliances required to maintain the desulfurization system operation in the event of a power failure.

The diesel generator shall be delivered in a permanent container housing. The delivered components shall include: cabinet of the output circuit breaker with the monitoring and control panel, including the DG protections, DG automatic start switchboard and the main circuit breaker, control and synchronization system, complete starter, maintenance-free battery, charger, water radiator, exhaust silencer, fuel tank for 12 hours operation at 75% nominal output without refilling including level gauge, oil fill, engine temperature sensor, retention sump, refueling pump.

The exhaust piping and diesel generator intake shall be equipped with a silencer. With the exception of flue gas emission and hot air emission, the diesel generator must not generate waste.

The start of the diesel generator must be ensured by using an autonomous battery that will be part of the diesel generator supply and the diesel generator must be capable of phasing into the respective electric switchboard.

The diesel generator must be equipped with a specified fuel consumption meter, i.e. it must have an approved, metrologically verifiable fuel consumption meter approved by the Czech Metrology Institute.

The operation of the diesel generator must be free of water use and sewage water discharges.

The start of the diesel generator shall be designed as automatic when the 400 V power supply voltage is lost; if necessary (tests, etc.) it will be possible to start the diesel generator from the central control room.

Additionally, a monitoring SW with a communication link to ŘS will be supplied, reporting operating and error conditions from the diesel generator's automatic switchboard (including fuel quantity monitoring in the tank).

The diesel generator container must be made in accordance with ČSN 38 5422.

The fuel used will be diesel according to ČSN EN 590 Motor fuels - Diesel fuel - Technical requirements and testing methods.

#### Drive control method

Motors and servo drives supplied within the WORK scope shall be controlled by default from the control system. If the control shall be enabled from another location (local control box), it will be ensured that the control is only possible from the selected location. Each control point shall contain a preset status indication.

The coding of the communicators and controllers by colors and complementary means shall be carried out according to ČSN EN 60073 ed.2.

The principles of control shall respect the standard ČSN EN 60447 ed.2.

#### Measurement of electrical quantities

Power and currents at all 6kV outputs shall be measured. The measuring instruments shall be placed on the switchboard, the same values ​​shall be transmitted to ŘS MicroSCADA.

The measurement range requirements for frequency converters are described in the chapter on the frequency converters.

Transducers of electrical quantities

Additionally, current and power transducers for measured quantities reported to the control system shall be supplied. The percentage load on the drives shall be reported to the control system, impulses from meters with impulse outputs, which shall be placed on the 6kV outputs of all the switchboards concerned, shall be fed into the electricity consumption metering balance.

These shall be located in the switchboard instrument space.

Transducers must comply with ČSN and IEC standards.

Auxiliary power supply to the transducers shall be 230 V AC.

Input ranges of the transducers must correspond to the outputs from PTP.

Transducer output is required in the range of 4 ÷ 20 mA.

Transducer accuracy shall be better than 0.5%.

#### Requirements for electric motors 0.4 kV

The electrical motors shall be made according to the standard EN 60034-1 ed.2 and related standards.

The motors shall be designed for continuous operation, with the exception of electromotors for shut-off fittings, which can be dimensioned for short-term operation.

The motors must meet the requirements of driven machines in both steady and transient states.

Constant speed motors shall be asynchronous with a squirrel cage.

Motors with connection to frequency converters must be designed for this connection.

The motors will preferably be supplied from one renowned manufacturer.

The motor power shall be adequate to the performance of the powered equipment. The operating factor, which is the ratio of the nominal power of the motor to the required power on the shaft of the driven machine at the maximum power requirement, shall be as follows, at minimum:

| Power requirement | Operating factor |
| --- | --- |
| up to 1 kW | 1.3 |
| over 1 kW to 10 kW | 1.2 |
| over 10 kW to 50 kW | 1.15 |
| over 50 kW | 1.1 |

Asynchronous motors with constant revolutions shall be able to supply nominal power at ± 10% voltage fluctuations or at frequency fluctuations of ± 1%. The motors shall be able to supply nominal torque at 70% drop in voltage for 10 seconds without dangerous overheating.

Asynchronous motors with constant revolutions shall be able to accelerate at terminal voltage equal to 85% of the nominal when the full load is connected. The accelerating torque in this state must be at least 5% of nominal.

The winding insulation class shall be at least F when used in class B.

The motor protection shall be at least IP54, terminal block IP54. When placing motors in places with environments with elevated protection requirements, the motor protection must be increased accordingly.

Electromotors with ​​controlled revolutions or electrical motors used for machines operating within a controlled range, shall be equipped with frequency converters.

Reliability and the number of operating hours of electrical motors without maintenance must be consistent with the maintenance and revision terms and the availability of the driven machinery.

Motors located in spaces with risk of explosion shall be designed in accordance with ČSN  EN 60079-14 ed.3, corresponding to the classification of hazardous spaces according to ČSN EN 60079-10-1.

#### Tranformers for nn switchboard power supply

Transformers for supplying NN switchboards (technological switchboards and switchboards for wiring in building) 6/0.4 kV shall be air-cooled, indoor versions, for maximum ambient air temperature 40 °C, with castors. In the event that the work shall consist of more than one absorber, each transformer shall be loaded to less than 50% of its nominal power in order to allow a backup in the event of a failure of one of the installed transformers.

| Parameter | Unit | Value |
| --- | --- | --- |
| Type of cooling in operation | 100% | AN |
| Nominal frequency | Hz | 50 |
| Nominal primary voltage | V ± % | 6,000 ± 2x2.5 |
| Nominal secondary voltage | V | 400 |
| Transformer protection | IP | IP 21 / IP 00 |
| Maximum ambient temperature | °C | 40 |

The power of the transformers shall match the maximum apparent power consumption of the powered devices.

The short-circuit voltage shall be determined by the contractor so that the transformer allows the voltage fluctuations for the appliances according to ČSN 38 1120 Art. 4 in transient and steady states, and so that the short-circuit stress in the substations is within the limits specified by the manufacturer.

Transformers shall be placed in the cabinets with minimum protection IP21.

Transformers shall be equipped with sensors for measuring winding temperature and a door contact.

#### Local control boxes

All motors and shut-off servo drives shall be equipped with local control boxes. These will be made of mechanically, electrically and heat-resistant, self-extinguishing, moisture-proof plastic with minimum protection IP54. The bearing structures for these boxes shall be made of galvanized steel.

The local control box function shall  enabled by a control element located on the appropriate box.

For local control, the boxes shall be equipped with a status indication ON/OFF, RESP. OPEN/CLOSED and buttons "On", "Off" or " "Open", "Close" and "Stop", and an indicator "Local control active". Further, the local control of the servo motors shall allow step by step control, opening and closing of the shut-off fitting servo motors in continuous steps.

Commands ON/OFF, OPEN/CLOSE STOP, or step by step control of the appliance shall only be possible from location where selected.

The control shall be made at 230 V AC. The control voltage shall be introduced directly into the control circuits in the respective switchboards.

#### Transition boxes

The boxes shall be made of mechanically, electrically and heat-resistant, self-extinguishing, moisture-proof plastic with minimum protection IP54. Only terminal boxes shall be inside.

Bearing structures for these boxes shall be made of galvanized steel.

Motors shall be connected to the boxes by tightly connected flexible leads.

Servo drives and solenoids shall be connected by means of movable leads with plugs.

The transition boxes can be combined with local control boxes.

Boxes located in spaces with explosion hazards shall be of a design in accordance with ČSN EN 60079-14 ed.4, corresponding to the classification of hazardous area according to ČSN EN 60079-10-1.

#### Emergency equipment STOP

In wet desulfurization areas, where required by appropriate standards, emergency stop buttons shall be placed.

#### Other electrical equipment and accessories

Other supplied electrical equipment and accessories must comply with standards, IEC and ČSN standards at minimum, as follows:

| Parameter | Value |
| --- | --- |
| Instruments for disconnecting and switching | ČSN 33 2000-5-537 |
| NN switching and control instruments | ČSN EN 60947-1 ed. 4 |
| Circuit breakers | ČSN EN 60898-1 to 2, ČSN EN 60934 ed.2 |

#### Electrical equipment control and monitoring

Control and monitoring of electrical equipment in desulfurization and preparation of limestone suspension shall be carried out from the central control room and from ŘS MicroSCADA.

#### ASŘTP power supply

- A new uninterruptible power supply (UPS) system shall be supplied to power the new ASŘTP equipment.

- The new UPS shall be powered from the newly supplied NN switchboard.

- Power supply requirements:

any failure of the ASŘTP power supply system shall not cause any problems in the controlled technology and there will be no changes in the positions of the actuators,

all components of the system shall be powered so that any instrument can be replaced at any time without having to disable other parts of the system,

the diagnostics of the power supply system shall be part of the diagnostics of the entire control system.

#### Protection against electric shock

Protection against electric shock shall be implemented according to the standards, ČSN 33 2000-4-41 ed.3: Protection against electric shock, ČSN 33 2000-4-473: Measures for protection against overcurrents, ČSN EN 61140 ed.2 Protection against electric shock - Common aspects for installation and equipment and standard ČSN 61936-1: Electrical installations exceeding AC 1 kV.

The equipment shall be installed in accordance with the standard ČSN 33 2000-7-729: Low voltage electrical installations - Part 7-729: Single-purpose facilities and in special buildings - Operating or maintenance spaces.

The design and layout of the instrumentation, the operating and supply voltage used must ensure the safety of both of the operator and the maintenance personnel.

#### Grounding

All supplied metallic, conductive equipment and all other components shall be interconnected effectively in accordance with valid legislation to ensure the protection of the conductive parts.

The grounding of all supplied equipment shall be made according to the standards for individual devices and according to ČSN EN 50522, ČSN 33 200-5-54 ed.3 and ČSN 33 2000-4-41 ed.3 and related standards.

All installed designed and convenient grounding elements, as well as all conductors providing grounding and connection, shall be appropriately marked.

#### Servo drives

Shut-off and control servo drives shall be electrical.

Power amplifiers for the control of servo drives shall be integrated directly into the servo drives.

The positions of the regulating elements (valves, flaps) shall be measured by sensors with a current output of 4 ÷ 20 mA.

Large shut-off servo drives and shut-off servo drives requiring step by step control approach during start up,  operation, and shutdown, shall be equipped by position sensors with a current output of 4 ÷ 20 mA.

No-contact sensors shall be used for position sensing - the use of resistive position sensors is not allowed.

The control circuits of electrical drives shall be protected by a separate fuse for every circuit.

The use of servo drives where the number of circuit closings is limited by the control software because of durability concerns, is excluded.

#### Cabeling

General requirements

All cables and conductors conducting electrical current shall be designed and dimensioned with regard to the type and magnitude of the transmitted quantity and the specific working conditions. It shall be ensured, in particular, that the working temperature is not exceeded, that no undesirable quantity loss occurs, that the cross-sections of the cores are within the economic limits and that the conductors are sufficiently strong.

The used hn and nn cables must comply with the requirements of ČSN. Termination of cables and bending and the method of installation shall comply with the conditions specified in ČSN and the cable manufacturer.

When introducing cables to switchboards, boxes, panels and appliances, the cable guard diameter must match the diameter of the cable installed. Cable passage from the switchboards to the cable ducts and spaces shall be provided with a fire partition.

Material and cross-sections of cable cores

Cables for control circuits shall have copper cores, power cables with cross-section of conductors of up to and including 35 mm2  - copper cores,  aluminum cores may be used for cables with cross sections from 50 mm2 and larger.

The design of the cable type and cross-section must be carried out in compliance with the requirements of the standards ČSN 33 2000-4-43 ed.2, ČSN 33 2000-4-473 and ČSN 33 2000-5-52 ed.2, and particularly reflect specific conditions:

short-circuit currents,

maximum continuous operating load,

allowable voltage drop,

environment in which they are installed (ambient temperature, humidity, presence of oils, chemicals, etc.).

Maximum temperature of the cores at any operating condition and at any point of the cable must not exceed the permissible values ​​prescribed by the manufacturer of the cable type used. The requirement is that in most cases it does not reach 80% of this value.

When determining the short-circuit stress, the most damaging conditions of source connections (i.e. the maximum possible short-circuit current) must be taken into account and also the tripping times of the protections, circuit breakers and fuses must be respected.

Maximum voltage drop must be in line with the power requirements of the appliances - in both steady and transient states.

- Cable insulation material

- Cable insulation material must meet the requirements for electrical insulation properties, adequate mechanical properties, resistance to temperature, humidity, chemicals and oils.

- VN cables shall be insulated by XLPE and PVC jacket. NN cables shall be all-plastic (PVC) with increased resistance to flame propagation in locations with increased fire risk.

- Cable structure

- The cable structure must be suitable for its application, in particular with regard to the mechanical resistance of cables to external influences, of sufficient flexibility and with protection against interference impact on low voltage cables. For control and signal cables connected to the control system, it is preferable to use twisted pair cables.

- In places where there is a danger of mechanical damage, the cables must be fitted with appropriate mechanical protection.

- Protection from induced interference signals

- It is necessary to apply complex measures to prevent the induction of disturbing signals in the control system by:

using suitable cable structure (twisted pair, cable shielding, etc.)

routing and installing power and auxiliary cables in separate trays; if it is necessary to rout cables of different voltage or current systems side by side, they will be placed into separate enclosed trays,

installing cables for low-level measurement and control signals (4 ÷ 20 mA, Pt100, thermocouples, etc.) in closed cable troughs,

reliably shielding the cables in one place (avoiding ground loops),

using materials and technologies resistant to electromagnetic and electrostatic interference (e.g. optical computer bus), etc.

Cable routing and laying

Cables shall be laid in one section. Where there is a need to divide or connect the cables, a special split or junction box or cabinet shall be used, with a degree of protection that shall correspond to the environment in which the cable splitting or joining is made.

No signals of different voltage levels shall be transmitted in one cable.

The cable routes shall be installed so that the maximum ambient temperature does not exceed the permissible values prescribed by the manufacturer of the type of cable used. The requirement is that in most cases it does not reach 80% of this value.

The cable ends shall be suitably protected from the environment (moisture or wetness, chemical influences, etc.) before installing the terminals.

The gangways and auxiliary supporting structures shall be steel, galvanized to protected against corrosion.

The space reserve in cable routes shall be minimum 20% above the designed requirement.

- Fire protection measures for cables and cable routes

- In order to reduce the possibility of fire and consequential damage, the following measures shall be taken:

functionally important cables, cables belonging to parallel, backup and emergency units shall be laid in separate routes,

cables shall not be placed directly on flammable material and must be separated by a sufficiently heat-insulating mat,

cable rooms and ducts shall be divided into fire sections by main fire partitions,

the main fire partitions shall be located at:

cable duct and bridge inlets to cabinets and shafts,

cable shaft inlets to the cable compartments,

partial fire partitions shall be located between the main fire partitions, in particular:

at crossings of cable routes,

at the beginning of branches,

at every 50 m of duct length,

pipe conduits in cable compartments, ducts, shafts, bridges, and cable conduits from the switchboards to cable compartments shall be sealed by a fire seal with the same fire resistance as the surrounding building structure,

cable conduits in floors, walls and at the points of entry into the switchboard must comply with ČSN 33 2000-5-52.

Cable marking

Cable marking shall be performed in compliance with the KKS methodology.

A uniform numbering system shall be implemented for electrical connections of all control and instrumentation equipment.

At both ends of all cables, labels of suitable insulating material resistant to moisture and oil shall be installed, on which the following data shall be clearly and legibly indicated (in the order shown):

from where the cable leads,

cable number,

type of cable,

where the cable leads.

These data must be the same as those used in all documentation processed by the CONTRACTOR.

Cables and cable routes for control cabling and for power cabling shall be appropriately labeled every 20 m of length and on both sides of the fire partitions (in accessible places); along the route cable marking of the whole bundle is sufficient, at cable ends and fire partitions cables shall be marked individually.

Cable labels must remain legible and fastened to the cable for the service life of the cable in the given environment.

Marking on the cable wires shall be implemented by clamps designating the terminal and terminal block. The terminal blocks shall be numbered. Unconnected wires shall be labeled "Reserve".

#### Cabinet mechanical design

The cabinet design must reflect the mechanical stress during operation and transport, electrical, thermal and short-circuit stresses and must be resistant to environment where used.

All cabinets shall preferably be of the same design.

When mounting electrical items in the switchboard, if the construction layout allows, use of DIN rails is recommended.

Measuring instruments monitored by the operators must be positioned so that the data on the scales and displays are readable. Instruments for general readings shall be located in heights of 1200 to 2000 mm and for precision readings in the range from 1400 to 1700 mm.

Manual control instruments must be at a height allowing easy manipulation. This corresponds to a height of 400 to 1800 mm above floor level depending on the nominal current of the instrument. Emergency buttons and signal fittings shall be located at a height of 1400 to 1500 mm, other button and signal fittings at a height of 900 to 1700 mm.

Terminal blocks must be clearly arranged, accessible and permanently marked. Terminals and terminal boards must be placed at least 200 mm above the bottom of the switchboard.

Only one wire shall be connected to each terminal (unless the terminal is designed to connect multiple wires). The cables shall be attached at the point of cable entry into the switchboard by fixed clips, such as SONAP.

Where possible, clamps with spring connections (not screw clamps) shall be used.

The control system cabinets shall be equipped with a transition terminal block between the power cable and the system cards. It is not allowed to connect the cables directly to the control system cards. The terminals of the transition terminal blocks shall have disconnecting design.

Each cabinet shall have minimum one grounding point distinctly and durably labeled for connecting the ground wire of sufficient cross section.

The cabinets shall be equipped with a sufficiently dimensioned strap for easy connection of all the shielding wires of all entering/outgoing cables. The strap shall be electrically insulated from the rest of cabinet structure and will be color marked according to the standard.

The cabinets shall be also equipped with a suitable system of connecting terminals (or other connecting elements), internal distribution and the arrangement of connecting cables.

The cabinets shall have two primer coats and one outer coat. (The quality of execution and color solution are subject to PURCHASER´S approval).

The direction of opening of the door must correspond to the layout, i.e. it must be adapted to allow easy access to the cabinets. If the cabinet width is greater than or equal to 1000 mm, the door shall be split.

If necessary, where natural ventilation is not sufficient, the cabinets shall be air-conditioned.

Each cabinet shall be marked in the upper left corner with the KKS code, the input switchbay of switchboards also by verbal description.

A list of appliances and equipment, including the KKS code, shall be placed on the face of the door. A matching list shall be on the inside of the door, complemented by the KKS code specification of the appliance location.

For modular cabinets, the terminal boxes shall be located at the rear of the switchboard and the switchboard shall be equipped with a rear door on hinges.

All switchboards shall be provided with asbuilt documentation on the inside of the door. This mainly concerns the connection of terminal blocks; for transducer and transfer relays cabinets also their wiring. The individual drawings shall be sealed in plastic covers.

#### Electrical equipment marking

All elements shall be marked by a tag with verbal description and the relevant KKS code. The tags shall be made of PVC material with engraved description and visibly placed on the relevant technological element.

### SKŘ – instrumentation and control system

The wet desulfurization control systems are concentrated in the process system PS 14 - SKŘ - Instrumentation and control system. Any additional subdivision of PS 14 structure may be proposed by the CONTRACTOR proposed in the DESIGN, after an agreement with the PURCHASER, also the possible transfer of some SKŘ technical components, physically delivered as part of the process technological equipment within the respective mechanical and process PS.

#### SKŘ basic concept

SKŘ shall consist of a control system and operational instrumentation (metering devices and actuators) interconnected by data and power cabling into one operational unit that ensures automated, reliable, long-term and safe operation and monitoring of all desulfurization technologies.

The basic process technology control system shall be DCS (distributed control system) whose architecture, performance, application and other features shall meet the requirements of this specification.

DCS may be combined, in justified cases, with autonomous components for the control, protection and monitoring of equipment  based on PLC, where the component was developed for a specific purpose or where it is part of standard equipment of special equipment or packaged units and supplied as a standard equipment for the management, protection and monitoring of these process technology systems.

In this case, components  based on the same HW and SW as is the DCS and programmable by DCS engineering tools are preferred.

All of these components must be integrated into the DCS structure so that it can control and monitor all technology in a coordinated way by DCS and its HMI tools.

For the entire set of controls used to control and monitor process technologies (i.e., DCS, autonomous PLC-based resources and dedicated systems), the common term "control system" (ŘS) is used in  this specification.

The wet desulfurization control system shall be integrated into the existing TKY Honeywell Experion PKS control system.

#### Method of control, control locations

Central control room

The ŘS shall be designed to enable monitoring of all process technologies, with the exception of operations requiring direct supervision and control, from one location - the central control room.

The workplace of the system engineer shall be also set up in the control room.

Local control points

ŘS will be supplemented, where necessary for safety reasons or for testing, operation and maintenance of the controlled equipment, by local control tools. It must be ensured that it is not possible to control the same device from more than one location at a time.

These include in particular:

Local control panels or terminals

These tools shall only be used where the equipment control requires direct supervision, where necessary for service reasons, possibly for special equipment (production and shipping of energo gypsum, in dry ash loading station, or other places as required by operation control needs).

Local control boxes for individual drives

Important motors and shut-off servo drives shall be equipped with local control boxes or directly equipped with local controls for local control.

Refer to Chapter 4.3.4.12 for local control boxes.

Local emergency stop buttons

Where necessary for safety reasons, local emergency stop buttons shall be installed in operation areas to allow emergency stop of the machinery.

#### Human-machine interface (HMI)

HMI shall be designed for single-operator process technology control. Control and monitoring shall be integrated into the operator environment of boilers K06 - K10. The operator environment of the newly supplied operator's workplace shall allow the management of the new desulfurization technology from any KY II boiler technology operator's station.

The control room space shall be equipped with the following operator communication means:

One (1) operator station with two 24" 16: 9 industrial wide screen monitors (part of DCS) to control and monitor all technological equipment.

The operator station shall be functionally equal to the existing operator stations so that from each of the stations it is possible (depending on the access rights of the operator) to control and monitor any DCS-controlled process technology equipment.

One (1) PC-based engineering workstation for parameterization, programming and maintenance of the ŘS system with the possibility of use as a backup workplace for operators.

Conventional controls

The control room shall be equipped with the necessary conventional emergency shutdown controls, a fire alarm button, etc., which shall allow control of the connected equipment independently of the operator stations. These elements shall be located within the immediate reach of the operator.

The control room shall also be equipped with all the tables and panels for placing/installing the above described operator communication means and other necessary furniture, including operator´s chairs with armrests and head rests for permanently present operators. The operator's desks shall offer sufficient  space for the placement of telephones and documentation.

The operator station shall communicate directly with the ŘS control unit. It is not allowed for the station to communicate via a third device - a server,  PC, etc.

The mixing center space shall be equipped by:

One (1) operator station with two 24" 16: 9 industrial wide screen monitors (part of DCS) to control and monitor all mixing center technology.

Control touch panels shall also be located in the energo gypsum production and shipping station, in the dry ash loading station, or at other places as required by operation control.

#### Level of automation

- ŘS must ensure automatic and safe operation of all process technologies delivered within the WORK scope.

- All handling that does not necessarily require on-location supervision must allow remote control from the DCS operator station. To achieve this, it is necessary to equip the technology with the necessary sensors and servo drives (control valves with control drives including all auxiliary devices) with the possibility of remote signal transmission to the control system. Walk through inspection is permissible only occasionally, namely 1 x in 8 hours, and when starting and stopping the equipment.

- The technology control shall be designed as multilevel, with the following top to bottom hierarchy:

Start-up, shutdown and coordinated operation of desulfurization as a whole.

Start-up, shutdown and coordinated operation of individual operation systems (PS).

Start-up, shutdown and coordinated operation of individual equipment sets and equipment items including related accessories. At this level, automatic actuation of mutually backed-up process technology equipment shall also be designed.

Control of individual actuators.

#### Basic ŘS functions

- The supplied ŘS shall be equipped with all tools to provide the following functions:

data collection from the process (measurement, technology status)

control and monitoring of the process technology delivered within the WORK,

monitoring of electrical power and own consumption of desulfurization,

monitoring of selected technology state data, supplied by the CONTRACTOR as part of technical equipment of buildings, such as:

ventilation and air-conditioning control systems,

heating of buildings,

monitoring of auxiliary operations

monitoring of signals from special equipment supplied within the WORK scope, such as:

electronic fire alarm system (EPS),

emission monitoring system,

long-term measurement and calculations of operating and balance values,

data upload to UE a.s. computer network, (data export from the system - status of main process technologies and desulfurization operation states to the Honeywell archiving SW PHD),

on-line diagnostics of ŘS,

communication with operators through DCS operator/engineering stations,

communication with operators through conventional controls,

external communication with all downstream devices.

- The scope is as follows:

- Data collection includes in particular:

processing of measuring signals from operation, including their linearization, filtration, their conversion to technical SI units, creation of limits and fault signals and detailed diagnostics of selected input signals.

- Control functions include in particular:

discreet control,

continuous control including cascade controllers,

protective functions:

technological blockades and protection of individual machines,

protection of individual technologies as well as the protection of interconnected operational units or operational sets.

- Monitoring functions include in particular:

display status of technology and electrical technology including instantaneous values ​​of the measured quantities,

special screen for each processed problem, concentrating information related to the given problem,

processing fault indication signals with priority sorting and suppression of undesirable signaling,

archiving function with the possibility of analyzing historical data,

display and archiving of event sequences,

the generation of time lines of process variables, both in real time and using data from the archive (trends of functions y = f (x)),

calculations of derived quantities,

monitoring of operating hours of selected drives,

creation and printing of reports, charts, protocols, etc.,

preparation of data for operational and economic calculations,

special data sets presented at the maintenance terminal,

potentially other functions.

- Measurements and calculations of operating and balance values ​​include, in particular:

material balances,

measurement of consumed electrical energy.

- The on-line ŘS diagnostics includes in particular:

continuously and automatically running ŘS diagnostics capable of detecting hardware failures as well as software changes (damage) and providing detailed information on the detected error and its location to the level of the individual system card.

- It will ensure at minimum:

during commissioning (including restarts) - checking the correctness of the HW functions and status and checking the configuration of the embedded SW,

during operation - on-line check of HW functions and status, performed sequentially so that the complete HW status (i.e. correct CPU function, integrity of all memories, correct power function, proper function of I/O modules, etc.) shall be checked approximately within 10 minutes,

continuous control of communication, based on diagnostic information contained in the communications transmitted and on the basis of methods capable of reliably detecting a failure of the connection,

checking of all analogue and binary values ​​so that the value and value converted to SI units is displayed at any time,

algorithm modification online without the need to shut down the technology.

immediate and automatic ŘS response to problems diagnosed on-line, in accordance with the principles of a "fail-safe design" (e.g. issuing incorrect instructions and incorrect information must be prevented);

processing and presenting diagnostic information from ŘS in a uniform manner on the respective service and maintenance terminals.

Control and monitoring functions shall cover all possible equipment operating conditions (start-up, shutdown, normal operation, fault states ...).

Monitored quantities shall include all data obtained from the operational measurements, internal ŘS diagnostic data of the control system, data obtained by diagnosing ŘS input signals and the connected special systems of the PURCHASER.

All media inputs and outputs to individual PSs and all values of the quantities monitored by the air protection system must be measured, archived and balanced.

Communication tools include all HW and SW resources needed to provide the above functions, including appropriate optical or metallic cabling.

#### ŘS architecture

Distributed Control System (DCS)

ŘS shall be based on DCS built on a unified HW and SW platform of a renowned manufacturer.

Real-time DCS shall consist of autonomous microprocessor-based stations capable of stand-alone operation, independent of the function of the other stations.

These stations shall communicate with each other via a backed up (or otherwise securely protected from connection failure) data network.

The individual functions of the system shall be appropriately distributed to the individual stations to minimize the impact of any failure of any of the stations on the controlled process.

Where appropriate, not only functional but also spatial decentralization of the system shall be implemented. A solution is possible where part of the system intelligence is distributed down to the level of intelligent units located directly in operating equipment.

DCS, including related devices, must be designed with respect to the "safe operation" principle, i.e. any local failure (signal loss, power supply failure, control or I/O card failure, failure of one of the stations, etc.) must not lead to an unnecessary process technology shutdown, to a long-term restrained operation or to the emergence of dangerous or hazardous situations. In the event of a total system failure, the process technology must be brought to a safe state.

ŘS must be open - it must allow further expansion of the system hardware configuration and the integration of third-party devices using open industry communication standards such as ETHERNET, PROFIBUS, MODBUS, including direct integration of alarms and events without duplication of data from one system to another.

The system must be configurable on-line - it must allow on-line changes in application software and of all parameters. At the same time, it must be possible to replace any faulty ŘS component while the corresponding redundant part shall be active. Modular solution is required so that repairs may be implemented by replacing faulty modules in operation, without the need to restrict operation or shut down the device.

No combination of input/output signals of internal states or operator commands shall cause the system (or any part thereof) to be blocked.

Depending on the role of individual DCS component elements, the system may be structured as follows:

Automation stations for process control including interface between DCS and process (I/O)

Communication system providing data transfer among DCS stations and data transfer among DCS and downstream digital systems

Stations providing human-machine interface (HMI) function, including:

operator stations

engineering workstations

servers for operator and archiving purposes

Autonomous PLC-based devices

It is acceptable that, under the conditions specified in Chapter 4.3.5.1 (SKŘ BASIC CONCEPT), after consultation and with a written approval of the PURCHASER, some technological subsystems shall be equipped with autonomous devices for the control, protection and monitoring based on  PLC or simple logic controllers

These may be subsystems such as fabric filter control, and similar.

These resources must be fully integrated into DCS. This means that as a priority they must be equipped with the same type of processor or from the same manufacturer and connected to the main process DCS bus or must ensure their connection to the DCS processing station using open industrial communication standards such as ETHERNET, PROFIBUS, MODBUS. OPC communication is not allowed for communication among the control and monitoring systems.

The transmission of important signals e.g. for blocking and protective functions shall be implemented by directly connected signals. All safety control functions shall be secured by a HW connection, independent of the ŘS function.

Preferably, their programming using the same programming tools as DCS (from DCS engineering workstation) should be used.

#### Component redundancy

Where the requirement for redundancy of the individual SKŘ components is not specified in this  Supplement to the CONTRACT, redundancy shall generally be at least on the level of:

operator stations, incl. servers for operator purposes, if used,

communication routes and nodes (servers, buses, communication modules, switches, etc.)

processors of control (automation) stations of important equipment, in particular:

where a processor failure could compromise the operation of the desulfurization or cause loss of production,

I/O modules for technologically important operating units (operating sets) or protective systems,

selected sensors of process quantities (to be connected to different I/O cards),

power supply modules.

For redundant components, smooth and impact-free transition from master to backup and vice versa shall be ensured, without the need for operator intervention.

Where possible, redundant elements shall be installed in geographically different locations.

#### Requirements for the design of ŘS main parts

DCS Servers

The use of DCS servers in the control system architecture is allowed.

Server configuration shall be with redundant connectivity and configured so that they can be used for process technology control.

In the event that the control system already used in the heating plant shall be supplied and if it is expected to be incorporated into the existing HW structure, and which is already equipped with sufficient capacity redundant DCS servers, new DCS servers are not required.

A modification of the operator's workstation from the DCS server requiring intervention at all operator stations is not allowed.

DCS servers shall be the source of a time stamp for operator stations and the engineering workstation.

DCS servers shall include a license (each server) to run the operator environment identical to the operator's station.

The DCS server shall shall include a local kernel based virtual machine in a rack configuration with switching to both servers.

Operator stations (part of DCS)

These stations are the basic interface between the operator and the process. Each OS includes its own computer station, monitors, keyboard, and a pointing device (mouse).

All OS monitors must be of the highest industrial quality, designed for continuous operation.

The keyboard must have normal QWERTY functions plus national keys for the Czech language.

Any OS shall allow, based on the appropriate access rights, to run an HMI application of any process technology.

OS screens shall allow the display of on-line images from operating camera systems.

Mode of display on station monitors

The display of media, actuators and values ​​shall be identical to the existing K6-K10 boiler visualization.

The values ​​of all measured quantities shall be preferentially displayed on the screens of all stations in the physical units of the International Measurement System (SI).

All information on service station screens interfacing with the operators must be in the Czech language, as well as all printed reports, protocols, etc. English may only be used for system screens of the system engineer´s workstation. Each Czech letter must be accurately displayed, including diacritical marks.

- Database and system integration (part of DCS)

- A global database is required.

- The management and configuration of alarms and events must be global. Each alarm must be configured only once for any operator station. Confirmation of one alarm at one operator station must ensure confirmation of the same alarm at all operator stations. Separate alarm databases at individual operator stations are not allowed.

- Additionally, the supplied system operation history module shall store any and all measured and calculated values ​​and device statuses in an archive for later analysis. The archive shall have the capacity to keep all the events and trends entered for the  minimum period of 1 month, and allow long-term archiving of selected data.

- The archiving operation must be completely automatic, independent of the operator.

- Using historical data, it must provide comprehensive information on:

equipment operating conditions prior to failure,

course of important variables before and after failure within given period (post-mortem),

operator´s actions related to the failure.

Engineering workstation (part of DCS)

The engineering workstation shall provide all the engineering tools and hardware resources necessary for the configuration, operation and maintenance of the system by PURCHASER´S personnel.

If the engineering workstation function is performed by DCS servers, an engineering workstation is not required.

The design (including the LCD monitor) shall correspond to the operator stations, shall allow taking over the operation of any OS, but will be equipped with only one (1) monitor.

The workstation shall allow the function monitoring of all automation stations or potentially servers connected to the bus and initialize and restart the system. It must include software for analysis of all connected stations, database management, management and configuration of intelligent operating devices (according to the FDT/DTM or EDD standard), initialization and configuration procedures.

- This function includes in particular:

displaying detailed information about the status of individual stations,

graphics configuration for the operator station in a graphic, interactive way using symbol libraries in an on-line status of the system,

configuring application software for individual stations and editing them on-line, enabling:

generating a database,

creating control algorithms in a graphical manner,

configuring different screen views at the operator station,

defining data for archiving including determining the sampling period, method of storing (hourly, daily averages, etc.) - configuring different reports and protocols,

introduction of system and application software into individual stations,

prior to the final transfer of the modified algorithms to the automation stations, it must be possible to simulate this modified logic using actual input variables with the output disabled (so-called "dry run"),

create documentation of the system actual status (hardware and software configuration).

Access to this station shall be protected by passwords corresponding to the  different levels of access rights

- Automation stations (part of DCS)

- The type and number of automation stations shall be established by the CONTRACTOR based on the requirements for reliability, redundancy, required system reserves (see Chapter 4.3.5.10) and taking into account the computational capacity of the stations.

- The automation stations shall control important PSs, designed with redundant power supply,  processor unit and a communication interface. They shall be linked through a redundant communications network.

- The stations and its programs must remain functional even if communication with the operator station or other automation stations is interrupted.

- The application programs of these stations must be stored in a power fail safe memory (FLASH).

- The stations shall be equipped with self-diagnostics up to the level of individual units and their inputs and outputs.

- The range of I/O units must be able to receive and transmit all kinds of standard measurement and control signals.

- The input side of the control systems must ensure the resilience of the system input against intrusive 500 V voltage, at minimum, and a short-circuit at the sensor terminals.

- For I/O units without backup, multiple important devices (especially where mutual back-up technology devices are involved) must not be connected via one I/O unit.

- Redundant input/output units must always be connected only via a redundant communication network.

- The number of inputs/outputs per card must not be greater than 32.

- The system must allow for the exchange of defective cards under voltage without affecting the controlled process.

- The input analogue unit must provide, at minimum:

filtering and converting the input analogue signal on the bus,

galvanic isolation of inputs from the bus,

conversion of A/D converters minimum 12 bits,

calibration and reset with automatic parameter setting according to a reference value,

evaluation of input signal limits with the possibility of remote setting of limits and hysteresis through the bus (may be solved also in the CPU),

signal filtering and suppression of 50 Hz frequency especially and higher harmonics,

ability to power sensors with current loop,

unit self-diagnostics, such as short-circuit diagnostics and analogue card loop disconnection.

For systems not using microprocessor-based input analogue units, some of these functions (limit evaluation, signal validation, correction, etc.) can be performed within the CPU.

The input binary unit must provide at minimum:

filtration and conversion of the input binary signal on the bus,

galvanic separation of inputs from the bus,

signaling the state of each input signal on the unit,

any polarity of the common pole,

two-wire connection of contact inputs,

unit self-diagnosis.

The output analogue unit must provide at minimum:

galvanic separation of the output analogue signal,

standard output voltage or current signal 0 ÷ ± 10Vss, 0/4 ÷ 20 mA,

evaluation of output loop break,

short-circuit protection at output,

unit self-diagnosis.

The output binary unit must provide at minimum:

galvanic separation of the output binary signal,

signal status of each output signal,

unit self-diagnosis.

The failure of one channel of the system I/O unit must not impact the operation of other channels in the same unit.

PLC based autonomous controllers

Autonomous PLC-based controllers are subject to the same requirements as the DCS automation stations. Any exemptions are subject to approval by the PURCHASER.

Communication

The data communication between the different levels of ŘS involved in the management of control and monitoring functions should be deterministic, so that the requirements for data flow and the properties of its behavior are independent of process technology events. If deterministic communication shall not be used, the data transmission lines must have such transmission capacity that they do not overload, lose data, or cause unacceptable data transmission delays, even at maximum data transmission loading.

The integrity of data structures and protocols used in transmission lines must be such that the system reliability is not significantly reduced by bus communication errors or collisions in access to shared devices such as data busses or shared memory for redundant processor systems.

All communication within the supplied control systems as well as between the supplied control systems and the downstream digital systems of the CONTRACTOR with specific functions (emission monitoring system, etc.) must use internationally recognized protocols. Selected protocols must support fault checking and troubleshooting.

For communication networks, industrial Ethernet with a communication speed of min. 100 Mb/s is preferred.

#### Requirements for specific functions

Protective systems of main desulfurization process technologies

The CONTRACTOR shall, when designing the equipment, take into account unplanned operating conditions, such as switching off the desulfurization fan, temporarily elevated flue gas temperature, vacuum and pressure fluctuations, total power supply failure, etc., and suggest measures for their control in the DESIGN.

Concurrently, the WORK shall include tools for diagnostics of non-standard equipment states and the associated automatic protection systems that, when a non-standard state potentially resulting in equipment damage or a threat to the safety of persons and operations is detected, shall take the necessary action to bring the device to a safe state.

Coordination of new and existing equipment systems

In the desulfurization and boiler control system, a combined load regulator for the flue gas booster fan and flue gas fans of the individual boilers shall be implemented in order to prevent an unstable or pseudo-stable (i.e., with one fan operating with minimum load and the second fan operating with maximum load) system status.

Control, monitoring and logging of desulfurization electrical equipment

The control and monitoring of the desulfurization electrical equipment shall be addressed through the operator stations and other DCS tools. For this purpose, a SW system shall be created in DSC so that the system can perform at least the following functions in relation to controlled and monitored electrical technology:

Control:

remote control of circuit breakers at voltage level 6 kV,

switching on/off of transformer circuit breakers 6/0.4 kV,

remote control of main and back-up switchbays, NN transformer outlets in substations,

the possibility for the operator to release control from the local control cabinets,

diesel generator (DG) start remote control for test purposes.

The back-ups shall be selectable automatically and manually. Manual control shall enable operation of circuit breakers in the main and backup switchbays.

When backing up the substations (short-term power failure), the outage of the control system or technological equipment must be prevented.

Monitoring:

monitoring the state of switches and grounding devices in 6 kV substation,

monitoring operating values ​​of all transformers,

monitoring of reports from the set of electrical protections, protection of 6 kV substations, NN substations, viewing the settings, viewing of event register,

monitoring of voltage and current loads of main and backup switchbays, 6 kV substations, VN/NV transformer outlets in substations and NN transformer outlets,

monitoring the state of the secured power supply (UPS, DG, LV switchboards),

monitoring the status and position of switches and important circuit breakers,

event and alert processing,

resetting protection,

reading and displaying the operating hours of main equipment items,

processing of different types of reports of el. energies, currents and outputs, etc.

Logging of electrical equipment states:

logging of the power system, relay protections and measurement data,

state and warnings of switchboards,

logging motor data, fault and measurements,

NN control voltage state and warnings,

etc.

Transfer of desulfurization data to TKY

Communication between the desulfurization ŘS and the TKY ŘS is assumed, ensuring transmission of information from desulfurization to, among others, the existing PHD archiving system in the UE.

#### Quantitative requirements for control system performance and reserves

| Parameter | Value/information |
| --- | --- |
| Response times |  |
| Sequence of events resolution (SOE) (including events occurring within the system, such as analog signal limits, operator intervention, etc.) | ≤ 10 ms |
| Time between the operator's instruction and output to the downstream device (actuator, electrical switchboard, downstream control system) | ≤ 1 s |
| Time between changing value of input variable and its display on screen | ≤ 1 s |
| Reserves |  |
| System memory reserve, minimum | 30 % evenly distributed throughout the system |
| System execution time reserve | ≥ 30 % evenly distributed throughout the system |
| Reserve in number of database items (tag, point) for all process variables and for all other data (including diagnostic) arising in ŘS, both for processor part and for the visualization part | ≥ 20 % |
| Reserve in the number of free inputs installed | ≥ 20% for each type of input signal used (reserve size of any of the system input and output cabinets may not fall below 5%) |
| Reserve in the number of installed free outputs | ≥ 20% for each type of input signal used (reserve size of any of the system input and output cabinets may not fall below 5%) |
| Reserve on each I/O module | ≥ 1 I/O |
| Reserve in unconnected I/O modules | Minimum 1 module of each type (number of free I/O on these modules is not included in the 20% reserve in the number of free inputs and outputs installed) |
| Wired reserve in the ŘS cabinets for installing additional I/O cards | ≥ 10 % evenly distributed throughout the system |
| Additional free space in cabinets (switchboards) usable for additional expansion of system capacity | ≥ 15 % |

#### Common requirements for ŘS

System dimensioning

The ŘS capacity (HW and SW), including related communication networks must enable the control and monitoring of all process technological equipment supplied within the WORK scope, while complying with the additional performance requirements and system performance requirements specified in this Supplement  to the CONTRACT.

The capacity of all communication devices must be designed so that, using all the specified reserves, no communication network or parts thereof are overloaded under any operational or fault conditions of all control and information systems supplied within the WORK scope.

PC and server based stations design

In order to install PC-based stations (operator stations, servers), it is required to use to a maximum extent the rack installation with connecting the operator terminal via an optical or metallic cable to the control room. The racks must be equipped with operation diagnostics (temperature sensors with alarm message, etc.), their design must correspond to the conditions in which they shall be placed (dust filters, ventilation).

Time synchronization and time stamps

All parts of the ŘS including any other digital devices used to control and monitor the WORK operation must be time synchronized using a single precise time source.

An NTP server synchronized with a GPS signal receiver supplied by the CONTRACTOR (PTP or SNTP protocol) shall be used as the precise time source.

Resilience to environment

All parts of the ŘS must be protected against the potential hazards associated with the operation of the desulfurization technologies and be capable of operating under the conditions in which they shall be installed. Account must be taken of all environmental conditions relevant to the installation.

The degree of protection shall be appropriate to the function of the device, the location of the device and the potential hazards.

Emission of electromagnetic interference

The emission of interfering electromagnetic fields from newly installed equipment shall not exceed Class A according to ČSN EN 55032 ed.2, from permanently operated monitors it shall not exceed Class B.

Resilience to electromagnetic interference

The control system must be sufficiently resilient to electromagnetic interference that shall occur in the installation space, including interference resilience to the use of portable FM and GSM transmitters of up to 5 W at a distance of up to 0.5 m from the device. Therefore it must be constructed from the elements eliminating interference - galvanic separation for components powered from other sources, consistent shielding of all components, preference of optical data buses, etc.

Process safety

SKŘ shall be designed and supplied in a manner limiting the risks arising from the process. All necessary precautions must be taken to prevent potential failures of equipment supplied within the WORK scope creating hazards for staff, equipment and surroundings either directly or as a result of error impacts on controlled technology during its start-up, normal operation, planned shutdowns, emergency shutdowns and outages .

#### SKŘ power supply

- To power the new SKŘ equipment, the supplied UPS shall be used (see PS 11). The power supply shall be 230 V AC and 24 V DC.

- Power supply requirements:

any failure of the system powering SKŘ shall not cause any problems in the controlled technology and there will be no changes in the positions of the actuators,

all components of the system shall be powered so that any instrument can be replaced during operation at any time without having to disable other parts of the system,

the power supply units shall be of modular design and shall have easily accessible and easily (without the need for tools) replaceable security features (fuses)

the diagnostics of the power supply system shall be part of the diagnostics of the entire control system.

#### Field instrumetation

General

The field instrumentation includes the supply of all complete measuring circuits needed for monitoring and automated technology control supplied by the CONTRACTOR, including all related and assembly components such as welded-on pieces, wells, counter-flanges, sampling valves, condensing vessels, separating vessels, impulse piping, power supply sources, transducers to 4-20 mA signal, etc., including throttles for installation in piping, inlets and outlets of auxiliary media, etc.

It also includes the supply of all sampling and measuring points including final assembly devices required for the GUARANTEE MEASUREMENTS and verification measurements (i.e. curtains, thermowells, pressure sampling, etc.).

The field instrumentation shall be supplied in such scope and manner that all manipulations that do not require on-location supervision can be performed from the operator stations and that all the variables to perform operational and balance calculations are provided.

Local display devices shall be supplied if their installation is required by special regulations (so-called legal compliance measurements), and wherever their installation is necessary or appropriate for checking the function of the equipment during maintenance and routine checks. Local display devices with an analogue scale of circular shape shall have a minimum diameter of 100 mm.

For remote sensors, the unification of instrumentation is required, meaning that for the same type of measurement sensors from several manufacturers shall not be used.

Unless prohibited by fundamental reasons, analogue pressure and differential pressure sensors with a standard 4-20 mA output signal, with HART configurable protocol and equipped by a display shall be used for the main process technology. It is also possible to use pressure and temperature sensors with a fixed range and output of 4-20 mA on lower level process technological units.

The temperature sensors on the main technology shall be preferably equipped with 4-20 mA integrated transducers installed directly in the sensor heads, configurable by the HART protocol.

The CONTRACTOR shall design and document the length of the calibration times for each element of the measuring chain. It is required that the length of the calibration period shall not to be less than 1 year.

Number of sensors

In the whole system, the principle of a single source of information, i.e. the use of signal from one sensor or the resulting verified signal from multiple sensors of one measured quantity for all system functions (sequential and continuous control, protection, archiving, etc.), must be applied. The number of sensors for individual measurements shall be designed by the CONTRACTOR with respect to the safety and reliability of the WORK operation.

Analogue sensor power supply

Sensors that do not require external power supply (such as analyzers, etc.) shall be powered using the test loop from the control system.

Sensors diagnostics

For all sensors, diagnostics shall perform two basic functions:

to inform both the maintenance and the operator about the correct or incorrect operation of the sensor and its accessories,

in the event of an incorrect operation, prevent the fault from spreading to the control circuit and further into the technology.

In case of uncertainty or loss of signal, ŘS must prevent the actuation of protection, back-ups and automatic instructions in the binary control circuits.

Measuring transducers

The measuring transducers shall work with a precision ensuring that the accuracy of the entire measuring chain (excluding the primary throttling devices for flow rate measurements) is better than 0.5% of the set range, also regarding non-linearity, hysteresis and reproducibility.

Sensors and pressure transducers shall work with an accuracy better than 0.3% of the measured range.

The transducer output shall not be grounded so that the signal line can be grounded uniformly (in the control system switchboard) to avoid additional errors.

Each transducer shall have its own, sufficiently robust housing protecting from harmful ambient influences and shall be mounted so that ambient vibrations do not affect its accuracy and reliability.

All instruments must be designed to operate under conditions of use and must be protected against specific external influences such as weather conditions, vibration, atmospheric corrosion, and similar.

If the transducer shall be placed in an environment with the possibility of freezing temperatures, the instrument must be sufficiently dimensioned for low temperature and secured against freezing, including the respective impulse piping. The robustness of the sensor design must match its location. If high temperature occurs in the space with instruments or cabling, it is also necessary to adapt the instruments and cabling.

Requirements for measurement connections

For each measurement of process technological parameters a sampling point must be provided (i.e. for example, a throttle for flow rate measurement with two sensors, each with a sampling point). Splitting can only be used in exceptional cases where two sampling points are not possible on the device.

The impulse piping (if supplied) must be dimensioned to meet the mechanical strength and stress requirements. Double separation, simple connection and drainage is necessary to ensure normal maintenance.

The dimensions of the impulse piping shall be selected from the standard.

The sampling piping shall be made of class 17 stainless steel.

The material and surface treatment of the impulse piping, shut-off fittings, and all connecting and auxiliary material shall be in accordance with the type of media to be measured and the surrounding environment to ensure corrosion protection and tightness of joints.

The basic requirement for minimizing the number of joints must be observed during assembly. Additionally, where there is mutual movement (due to the operation of the equipment) of the sampling point and the transducer, it is necessary to install attenuation loops (simple or double) during assembly.

Sampling points for measurements, sensors, transducers, and valves shall be installed to provide easy access, or possibly with an access walkway or ladder.

The impulse piping must be designed so that the measuring device can be disconnected without disconnecting or discharging the impulse piping using separation, test and metering valves.

The layout of the impulse piping must allow for easy disconnection of the measuring transducer for repair.

The impulse piping must have a minimum gradient of > 8% to allow air or gas bubbles to rise to the bleeder valve, and liquid or solid sediment to descend into the drain chamber. Generally, the pipeline gradient must increase with the viscosity of the media.

Impulse piping for differential pressure measurement must be kept mutually as close as possible to suppress ambient temperature impact. Piping diameter must be the same throughout the length from the sampling point to the sensor.

For all balancing measurements and verification of parameters (also chemical), a connection for a test instrument shall be provided. The connection must be threaded M20x1.5.

To measure temperature for the validation measurement, a separate well of the same immersion shall be provided as the operating measurement, extending above the insulation and with a cover to prevent contamination.

Each pressure sampling point on the process technology shall be terminated by a fitting (for pressures from 10 MPa doubled).

Ranges of measuring strings

Unless otherwise explicitly stated, all measuring transducers shall provide a functional trend of increasing output signal with an increasing measured quantity.

The measuring strings (signal sources, sensors, transducers) shall be designed so that the nominal value of the measured quantity corresponds to about 60% of the measuring range (the requirement does not apply for electrical measurements).

The measuring strings (signal sources, sensors, transducers, control system input parameterization) shall be designed so that even at maximum operating values ​​of the measured quantity (e.g. starting currents of motors, operating voltage higher than nominal), no error message in the measuring circuit is reported by the control system (input value outside the allowed range).

Temperature measurements

Remote temperature measurements shall be made by thermoelectric and resistance thermometers.

Resistance thermometers Pt 100 (TR) shall, depending on the installation (design with a thermowell or to a thermowell) be "with higher mechanical resistance" (shock-resistant). Configurable transducers with HART protocol shall be used at 4-20 mA. The location of the transducers shall depend on the location of the thermometers, but preferably in the sensors´ heads.

The thermocouples used shall be of the type J (Fe-CuNi) or type K (NiCr-Ni).

For direct measurement of temperature,  mercury-filled instruments must not be used and must be of a stainless steel design. It is also not allowed to use glass thermometers.

Pressure and pressure difference measurements

The sensors must allow remote calibration from ŘS by the HART protocol.

In exceptional cases for low-pressure measuring points where only binary signal is required, contact sensors may be applied.

Pressure measurement gauges on pressure vessels must bear the mark with the maximum operating pressure.

Quantity measurements

Quantity shall be measured by a suitable primary element (e.g. a throttle, velocity probe, vortex, etc. ...), HART protocol configurable differential pressure transducers to a unified signal followed by mathematical processing in the downstream control system (extraction and integration, or possibly pressure and temperature correction). In justified cases, a solution is also possible using independent mathematical members with an output to ŘS. Transducers of the quantity measurement sensors must be configurable by the HART protocol directly from ŘS.

The selection of the throttle arrangement for water and steam quantity measurement (point or chamber aperture according to the measuring point parameters) shall depend on the required measurement accuracy. The measuring apertures shall have class 17stainless steel discs.

For possible indication of lubricating oil and cooling water flow rates for the individual devices, binary flow indicators may be used in justified cases.

Each raw material or product silo shall be equipped with analogue and limit level sensors.

General requirements for incorporating primary elements into pipelines

To ensure the maintenance of primary elements, sufficient space must be left at the primary element installation point for possible inspection or replacement of the primary element.

Each primary element and shut-off fitting must be accessible from access spaces or platforms.

For the placement of a primary element, equal lengths must be provided before and after the primary element as prescribed by the standard or by the device manufacturer, reducing the straight length is not allowed without the approval of the PURCHASER.

In cases where clogging of the measuring part is anticipated and the measuring point allows it, the measurement shall be positioned so that it can be cleaned without disassembly.

In order to prevent damage to the primary element, it must be designed so that it can be removed from the pipeline before flushing and be replaced by a spacer. After completion of the tests, the spacers shall be dismantled, uniquely identified by their position and handed over to the PURCHASER for further use.

Level measurement

For sensors operating on the principle of differential pressure measurement, the requirements stated in section "Pressure and pressure difference measurements" above are applicable. Transducers with 4-20 mA current output with remote calibration possibility  (HART) shall be used. Exceptionally, limit state sensors with a switching contact can be used. Local water gauges shall be of the reflective glass design, or the clear visibility of the actual liquid level shall be ensured in a different manner.

Measuring levels in liquid storage vessels

The supplied storage vessels shall be equipped depending on their size with an appropriate number of suitable level sensors for continuous and limit level sensing. Data on levels shall be fed into the control system from the evaluation units.

Contact sensors

Contact sensors for measurements can be used only in justified cases.

The two-state sensors used shall be of such type and contact design that they can be connected directly to the ŘS automation circuit without the need for a transfer relay or other additional transducers. The use of switching contacts is preferable to enable diagnostics from the control system. Contacts shall be powered from the control system.

All contact sensors used to measure physical quantities and positions shall conform to the environment where installed.

Measurement of electrical quantities

The measurement of electrical quantities used for process technology control shall use electrical transducers placed in the electrical equipment switchboards, which shall be a part of electrical equipment supply.

#### Cabling

The requirements wiring and cabling design are provided in Chapter 4.3.4.22.

### Emission system monitoring

- The CONTRACTOR shall supply independent emission measurement monitoring systems.

- The automated emission measurement monitoring system (AMS) shall provide a continuous emission measurement that will continually measure the mass concentration of pollutant emissions discharged from TKY II during the calendar year. The results of continuous emission measurements shall be in the scope and manner established by Act No. 201/2012 Coll. and Decree No. 415/2012 Coll. continuously recorded, evaluated and stored. The data collected by continuous measurements shall be protected against alteration and shall be provided in the form specified in Decree No. 415/2012 Coll.

- The following continuous emission measurement systems shall be installed:

measurement of emissions exiting the absorber (wet stack) required by legislation (CO, NOx, SO2, TZL) and Hg emission measurement, the analyzers shall be located in the new substation (SO 03) building;

measurement of emissions at each boiler output after LF (dry stack) required by legislation (CO, NOx, SO2, TZL) and one measurement of Hg emissions common to all boilers, the analyzers shall be located in the existing analyzer room at the bottom part of the stack;

operational measurements at the absorber input (CO, NOx, SO2, TZL), the analyzers shall be placed in the new substation  (SO 03) building.

Measurement of flue gas flow rate and O2 content at the outlet of each LF and at the absorber outlet shall also be part of the emission measurements.

All sampling points shall be equipped with sampling flanges for one-off and validation emission measurements.

Probes, sensors and instruments used for emission monitoring shall be placed in a separate box. The location of the sampling points shall be chosen for measurement accuracy with respect to the required straight length of the flue gas duct before and after the sensor. Measurement information shall be recorded and transmitted to the existing boiler emission monitoring evaluation system.

The measured values and diagnostic data shall also be transmitted to DCS.

The emission monitoring system shall be powered from the UPS. The measurement system must be equipped with calibration devices.

More detailed requirements for the individual monitoring system emission measurements are provided in Amendment D01.

### Communication systems

#### Voice and data communication

The CONTRACTOR shall propose location of telephone sets and data sockets in the desulfurization premises

The telephones  shall be connected via separate lines to the existing telephone exchange.

A switch shall be placed in the desulfurization building, to which new data sockets shall be connected. This switch shall be connected to the existing UE switch via an optical cable.

The existing telephone exchange and the existing switch are located in the server room (see Amendment D05).

#### Electrical fire alarm system

The electrical fire alarm (EPS) shall be designed by extending the existing EPS exchange LITES MHU111.

Newly constructed buildings shall be equipped with automatic fire alarms. Push button fire alarms shall be located on the escape routes.

The fire alarms shall be connected to the existing EPS exchange.

EPS system concentrators are located in Building no. 33 Warehouse of small spare parts, the exchange LITES MHU111 itself is in Building no. 30 Fire station.

# Operational requirements

## Operational environment

In the spaces inside the buildings, the external influences (external influences protocol) must be determined by the CONTRACTOR according to ČSN 33 2000-5-51 ed.3 and the corrosive aggressiveness of atmosphere according to ČSN EN ISO 9223. The supplied equipment must be delivered in a design corresponding to the environment .

Equipment  that is not located inside of buildings must be of the outdoor design version.

## Operation personnel

A continuous operation is assumed.

For one shift, the following number of staff is assumed:

| Position | Number per shift |
| --- | --- |
| Operator | 1 |
| Current shift foreman (STK) | 1 |
| Occasional walk around service person | 1 |

This personnel must be able to operate the desulfurization in all modes of operation including start-up and shutting down the desulfurization.

The design of the WORK and character of process equipment automation must match this requirement.

## Operating modes

### Normal operation

The normal operating mode shall include all operating states including dynamic changes in the output of the boilers.

In the normal operating mode, the equipment must be able to operate in fully automatic mode while complying with the parameters of the products and with emission limits.

The equipment must achieve this performance at both maximum summer temperatures and minimum winter temperatures and over the entire boiler power output range.

The desulfurization products will be certified by the PURCHASER. Certification is assumed for the following products:

Stabilizate with ENGS at production 0% ENGS

Stabilizate without ENGS at production 100% ENGS

Stabilizate without LF fly ash (at ash production from LF)

Energo gypsum (ENGS)

The preferred use of stabilizate is for embankments and backfills in the construction of roads and for embankments and backfills in strip mine spoil dumps.

The assumed initial composition of the mixture for the stabilizate product is shown in the table.

Assumed percentage shares of stabilizate mixtures - indicative formula:

| Mixture | Ash | Lime | Energo gypsum (product purity CaSO4x2H2O cca 95%) | Dry matter | Mixture water (min) | Min. stabilizate moisture content Stabilizate/Dry matter | Min. stabilizate moisture content* water/(dry matter + water) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | 83.2% | 3% | 13.8% | 100% | 11.3% | 1.113 | 10.2% |
| B | 80.8% | 3% | 16.2% | 100% | 13.3 % | 1.133 | 11.7% |

* The minimum stabilizate moisture content is indicatively defined as the minimal moisture with respect to the water supplied in the energo gypsum suspension, it can be assumed that higher moisture content values ​​(in the 20% range) shall be required based on processing tests.

To design the process technology and actual balance flows, it is important to adhere as much as possible to the assumed formula, respectively to comply with it. The deviations must be discussed at the design and implementation stage.

In the design and implementation stage the CONTRACTOR must also take into account the following facts and adequately dimension the elements of the supplied technology:

The production of stabilizate is campaign-based (see the description above). The retention/storage volumes of the stabilizate components must be dimensioned accordingly.

The production of the stabilizate must be uninterrupted (continuous) up to the maximum capacity of the mixer (i.e. up to 200 t/h of the dry component). An interruption is accepted only at the operator's discretion, on the basis of a safety or blocking signal, or when swapping the operation of individual mixers.

During the continuous production, a continuous supply of all components, especially lime, must always be ensured in order to achieve the target (set) formula.

All control elements for the individual components must be capable of efficient regulation (or co-regulation) so that the output quantity can be influenced in the range 30-100%.

The ash flux (main component of the formula) is not stable. The main control signal for the formula is therefore assumed to maintain the ash mass flow, i.e. the regulation of the other components of the formula to be effectively set and dosed to achieve the required formula.

The production of the stabilizate shall allow for an optional adjustment of the output (required) moisture content of the mixture in the range of - 15% to + 20% of the initial formula.

In supplying water to the stabilizate mixture, the following requirements shall be reflected as much as possible:

• Saline water is fed by the existing route directly to the stabilizate, raw water as process water for the wet scrubbing technology. Water addition (according to formula) to the stabilizate is provided primarily by saline water and is supplemented by water from the wet scrubbing technology.

• Saline water is preferably used as a process water in the wet scrubbing technology, possibly supplemented by raw water. Water addition to stabilizatate (formula) is ensured primarily by water from the wet scrubbing technology and is supplemented by raw water directly from the water system to the stabilizate.

• All options must be appropriately controlled.

• It is always preferable to use the saline water within the above mentioned operating modes so that no waste is generated.

Water delivery to the stabilizate mixture will be implemented (enabled) in several ways based on the operator's decision.

• When producing stabilizate with energo gypsum, part of the water to wet the mixture will be delivered within the gypsum suspension. The remaining part of the water for the formula will be supplied from the water system or if convenient, via the scrubbing technology. The CONTRACTOR shall monitor the balance of all water consumption (wet scrubbing technology and stabilizate production) and water consumption for the formula delivered via the gypsum suspension for the assumed default formula.

• In the production of  stabilizate without energo gypsum (i.e. with the shipping of the energo gypsum in a dry state), water shall always be used to avoid waste. The CONTRACTOR shall thoroughly monitor the balance of all water consumption (wet scrubbing technology and stabilizate production) and water consumption for the formula delivered directly from the water system and through wet scrubbing technology for the assumed default formula.

• Deviations in the formula resulting from the variable amount of energy gypsum produced or respectively the supplied gypsum suspension will be balance checked for water consumption and must be approved.

• Formula variations resulting from the variable amount of ash supply (low power output, fuel change, separation of the LF ash component from the total ash production) shall be balance checked and specified as limit values ​​at which the consumption of saline water will be ensured.

• The PURCHASER reserves the right to specify the moisture content of the mixture and composition in more detail during project preparation based on research conducted.

- 	The shipment of the dewatered energo gypsum shall be conducted in campaigns, with the basic assumption of shipment in the same period as the agglomeration operation. The shipment mode will correspond to the technology retention quantities for wet and dry state. With regard to the requirements of the quality of the energo gypsum,  waste free technology and the options of supplying water to the stabilizate, process modes of water supply (saline or raw) and the provision of stabilizate wetting shall be assessed and specified. The permanent shipment of energo gypsum without the parallel production of the stabilizate is not anticipated in the long term. The permanent shipment of energo gypsum with parallel production of the stabilizate (see above and chapter 1.5.6) may be anticipated.

The dewatered energo gypsum shall be produced in the quality matching the standard of the so called FGD Gypsum (issued by EURO GYPSUM) while using the Type 1 limestone (chapter 1.8.1 – measured value).

| Constituent/indicator | Unit | Value | Note |
| --- | --- | --- | --- |
| CaSO4 x 2H2O | % mass | ≥ 95 % | Dry |
| CaSO3 x 1/2 H2O | % mass | ≤ 0.5 | Dry |
| MgO | % mass | ≤ 0.1 | Dry |
| Cl | % mass | ≤ 0.01 | Dry |
| Na2O | % mass | ≤ 0.06 | Dry |
| Moisture content | % mass | <10 | Original |
| ph | - | 5 to 9 |  |

Additional requirements: non-toxic, odorless, white color.

### Start-up

Start-up of the key desulfurization equipment nodes (absorber, limestone suspension preparation, etc.) shall be possible in an automatic mode.

### Shutdown

Desulfurization shutdown shall be possible automatically in the following modes:

For planned hot restart,

For planned inspection or repair (cold state).

Desulfurization shall also be automatically shut down by protective systems in the event of non-standard states.

### Exceptional conditions

Operation of desulfurization in case of power supply failure

In this case, it is required to ensure shut down the desulfurization and to ensure the operation of important equipment (mixers, etc.) by supplying power from the diesel generator.

Winter operation

The desulfurization system must operate safely and reliably even at low outdoor temperatures, i.e. there must be no device failures due to freezing of the equipment in winter. Therefore, the WORK design must include measures to enable the operation of the equipment at low temperatures without extraordinary measures such as the installation of mobile heating units.

These measures must also be sufficient to maintain the equipment at low temperatures for a longer periods of time in a shutdown but operable state.

All exterior flaps and fittings shall be made with regard to their use in winter months to prevent their immobility.

All flue gas duct flaps shall be made for use in the flue duct with respect to the presence of fly ash when the LF bypass is started.

# Maintenance requirements

## Basic requirements

All equipment shall be designed, built and installed to ensure the equipment availability within the meaning of Supplement 2 to the CONTRACT and so that its maintenance is simple, safe and as economically viable as possible, implementable by procedures in accordance with the Czech legislation, respecting specific conditions and time constraints for maintenance of the individual devices, and not creating risks for the availability and safety of desulfurization operations.

Therefore, procedures and resources shall be extensively applied in designing of the WORK to simplify and reduce maintenance costs and to achieve short repair times consistent with the equipment reliability requirements.

- These procedures and resources shall include in particular:

Use of maintenance-free equipment with minimal requirements for physical inspection and maintenance (e.g.: self-lubricating pump bearings, ceramic seals, etc.).

Limiting the number of devices with service life less than the total service life of the WORK. Their renewal must be possible within the terms corresponding to the required scheduled repairs.

Unification of technical components ensuring the same functions, limitation of spare parts assortment, substitutability of components.

Utilization of on-line diagnostics of process equipment such as the evaluation of temperature stresses on critical components, evaluation of lower than dew point temperature occurrences, etc.).

Extensive and automated on-line internal diagnostics of the electronic systems including on-line verification of measuring circuits.

Long-term monitoring and evaluation of the state of the equipment based on results of the measured data, diagnostic information, machine operating hours, off-limits operation time, etc., allowing preventive maintenance planning based on measured values ​​and trends, and to determine the time and extent of routine repairs.

The design of the WORK must exclude, respectively limit the need for the use of non-standard failure finding and troubleshooting techniques to a reasonable minimum.

Equipment shall be designed to minimize human labor and maintenance time.

In electronic systems it must be possible to replace the defective component while the corresponding redundant part is active. Modular solutions are required so that repairs can be performed by replacing faulty modules in operation without having to turn off the power supply.

The WORK must be designed and implemented in such manner that regular maintenance requiring equipment shutdown can be carried out at scheduled shutdowns of the process technology.

## Equipment diagnostics

The CONTRACTOR is required to design a system for critical equipment diagnostics and a method of indicating limit values for making decisions on equipment maintenance requirements. The supply of the diagnostics is subject to approval by the PURCHASER.

The control system must inform the operator in time about the malfunction of the equipment or changed operating parameters such as temperature, pressure, flow rate, concentration, etc.

## Lighting requirements

Devices requiring regular access for routine testing or maintenance must be sufficiently illuminated or fitted with built-in lighting (cabinets and switchboards). For work inside the device, a portable light with its own power supply must be provided (supplied) with a built-in rechargeable battery, or a power supply socket must be available in close proximity. The design and electrical covering must correspond to the environment (external effects) in the area where the light shall be used. However, fixed lighting is preferred.

## Worker safety

The WORK shall further be designed so that when carrying out maintenance, persons and property are not endangered, especially in order to:

Secure the equipment against undesired interference.

Provide equipment with potential hazardous gases presence with the capability for flushing with sufficient quantity of air or inert medium.

Inform the operator that the parts of process equipment are being shut off (e.g. for testing or repair purposes).

Double the installation of safety fittings where replacement is anticipated during operation and equip them with a mechanical locking system that will not allow both fittings to be closed at the same time. Keys to the locking device must be stored outside the normal reach of the operator (e.g. in a lockable box in the control room).

All uncovered rotating parts (such as pump couplings) and hot surfaces (above 50 °C) within the operator's reach must be provided with removable covers that will not allow touch or tangling of the operator.

In the event of personnel being exposed to chemical agents, or when eye-washing is necessary, first-aid kits shall be available at accessible locations, subject to all health and safety policies. The showers and washbasins are part of the equipment for the machine operators´ facilities. No special rinsing points are being considered.

Passages and corridors must have a clear height of 2.1 m minimum.

All premise must have marked escape routes in the form of lines on the floor, and these routes must be illuminated by emergency lighting even in the event of a power outage.

The operating voltage used in the equipment shall be such as to substantially reduce the likelihood of an electric shock. If exceptions are necessary, they must be substantiated and described in the technical maintenance procedures.

The maintenance and repair procedures must respect all safety-related regulations and restrictions resulting from applicable standards and regulations.

## Access requirements

Providing access routes and service structures for the equipment supplied within the WORK scope (passages, ladders, platforms, etc.) required for the operation and maintenance shall be a part of the WORK scope.

All parts of the WORK requiring operating manipulations or maintenance, must be accessible for operation and maintenance without the use of temporary structures (ladders and scaffolding).

This applies, among other, to the roof and stack installations and to the HVAC control units located under the ceiling.

## Transportation requirements

Sufficient capacity access roads shall be provided to allow the transport of special equipment, accessories and spare parts necessary for the maintenance and repairs of the equipment, including necessary transport packaging and means of transport to the place of use or installation.

Data on loading, location of support beams, or equipment anchoring shall be submitted for approval by the PURCHASER at the DESIGN stage.

The capacity of the individual monorail cranes shall be marked on the rails in yellow color large letters. Stable monorail cranes shall be provided as part of the delivery if the equipment cannot be transported by conventional means (forklift) because of space or weight constrains.

Lifting equipment with load capacity over 1.5 t shall be powered. Control cabinets shall be unbreakable and waterproof.

All lifting equipment must comply with the relevant Czech standards.

For heavy and large-dimension parts assumed to be transported during the installation of new equipment and/or replacement due to a serious failure, such transportation logistics must be developed, that after the completion of the WORK and the eventual related building modifications, the potential replacement of these parts shall not be constrained by the final state of the transportation routes and the lifting capacity of the lifting equipment.

It is required that safe transport and relocation of loads of more than 50 kg and/or with extraordinary dimensions requiring more than one person, is not needed during the standard maintenance operations.

Exceptions not meeting this requirement must be known in advance, the relevant parts must be adapted for such handling and fitted with manipulation handles, auxiliary supporting structures, suspension lugs, storage and transport aids, etc. according to the nature of the load.

## Special tool supply requirements

The CONTRACTOR shall equip PURCHASER´S maintenance by all special tools.

The manner of using the special tools shall be a part of management, operation and maintenance staff training and shall also be described in the maintenance work procedures.

Special tools shall be delivered in suitable, durable packaging including workflows and PTD for its checks and maintenance.

## Special instrumentation supply requirements

The CONTRACTOR shall equip the PURCHASER´S maintenance workplaces with all special instrumentation.

The supplied instrumentation shall be designed and constructed so that checking its technical characteristics is feasible with standard equipment without any doubt as to the correctness of the result.

The reliability characteristics of this instrumentation shall be higher in the prescribed mode of use than of the comparable supplied parts of the maintained equipment.

The supplied instrumentation equipment jointly with standard instrumentation shall enable all maintenance workflows to be carried out and must enable the full range of tests to be carried out in order to commission and start the equipment supplied within the WORK scope.

The manner of use of special instrumentation supplied by the CONTRACTOR shall be a part of PURCHASER´S management, operation and maintenance staff training and shall also be described in the maintenance work procedures

# Service life requirements

General

The PURCHASER assumes three (3) weeks maximum downtime of the process equipment to identify the technical condition of the equipment (routine repair - BO) every year to eliminate the identified defects. Longer outage (overhaul - GO) is assumed every ten (10) years.

It is required that the equipment operates without replacement of the decisive machines and equipment for at least 20 years, when operating desulfurization for about 8,136 (in the first year) and 8,256 (in the second and subsequent years) hours/year.

The desulfurization plant must be designed so that:

parts that can be repaired or replaced only during GO have a service life of at least 84,000 operating hours;

bearings, coolers, working elements of rotary machines (excluding suspension) in machines with an output exceeding 25 kW have a service life of at least 60,000 operating hours;

parts with service life of more than 16,000 operating hours have a service life of at least 26,000 operating hours (replacement at each third BO);

parts with service life shorter than 9,000 hours shall be repaired or replaced during operation.

Material quality, construction and design, dimensioning of individual equipment items and its components, internal corrosion protection where necessary, and other measures must meet these requirements.

Civil part

Supplies for construction, parts of buildings, structures and products must meet the basic  requirements of the Government Decree No. 163/2002 Coll. Determination of technical requirements for selected construction products (Annex No. 1), as amended, by Government Decree No. 312/2005 Coll. within the meaning and in accordance with Act No. 22/1997 Coll. on technical requirements for products, as amended, and related implementing decrees.

Fabric filter

The service of the filter hoses shall be at least 24,000 operating hours while complying with the limit of 7 mg/Nm3.

Flue gas scrubber, rubberized parts or parts protecting the absorber internally

The service life of this equipment shall be at least 24,000 operating hours.

Fans

The ID fan impeller shall have a service life of at least 84,000 operating hours.

The fan bearing service life of at least 40,000 operating hours at nominal loading is required.

Pumps and mixers

Larger size ball and roller bearings of pumps and mixers and pump impellers must have a service life of at least 60,000 operating hours at nominal loading.

# Fire protection requirements

## General principles for fire safety design

The DESIGN shall, among other, include a summary report with a PBŘ section. The documentation for the individual SOs, as well as for PSs, must include a PBŘ section processed according to regulation No. 246/2001 Coll.

The PURCHASER requires that the CONTRACTOR proposing the WORK does not assume the presence of the company Fire Brigade/Rescue Service (JHZSP) at the plant premises, although such outfit is currently present on the site. This relates to the process technology proposed and to all the stages of the process design in the respective sections concerning the fire safety design.

Requirements for the fire safety design of the WORK are part of Supplement 01.

# Health and safety protection requirements

The CONTRACTOR shall eliminate as much as possible any risks arising from the process. The process must be safe and all necessary precautions must be taken by the CONTRACTOR to eliminate any hazards to personnel, equipment and surroundings during the commissioning, normal operation, planned shutdowns, emergency shutdowns and outages. Venting systems shall address safe discharge of released gases or vapors.

The desulfurization plant shall be designed and implemented by the CONTRACTOR in accordance with the applicable safety regulations, regulations and ČSN standards, as amended. Also, all desulfurization operations shall be carried out in accordance with these regulations, decrees and standards.

In the design and during implementation, all effective OHS ordinances and regulations for specific work and activities must be taken into account and respected (especially the ČÚBP Decree No. 48/1982 Coll., laying down the basic requirements for the safety of work and technical devices, in particular Government Decree No. 101/2005 Coll., on detailed requirements for workplaces and work environment, Government Decree No. 362/2005 Coll., on detailed requirements for OHS in workplaces with the hazard of falling from height and to depth and all related other decrees, standards and regulations, as amended by subsequent implementing and amending regulations). The CONTRACTOR is obliged to observe with respect to OHS within the meaning of the Labor Code (Act No. 262/2006 Coll.) and the related Act No. 309/2006 Coll., on detailed requirements of OHS (within the meaning of the EEC Directives) to comply especially with  Government Decree No.361/2007 Coll. establishing conditions for protecting employees at work, Act No. 258/2000 Coll., On the protection of public health (as amended, and in particular Government Decree No. 272/2011 Coll., on health protection from adverse effects of noise and vibrations ), Decree of the Ministry of Health No. 432/2003 Coll., establishing conditions for the classification of work into categories, limit values ​​of the biological exposure test indicators and the requirements for reporting work with asbestos and biological agents, and Government decree No. 378/2001 Coll. establishing detailed requirements for the safe operation and use of machinery, equipment, instruments and tools. Increased attention shall be paid to work with electrical and lifting equipment and construction machinery. The operators of this equipment and machines must have the appropriate certifications and qualifications.

The proposed DESIGN shall respect in particular:

- Act No. 258/2000 Coll., on the protection of public health and amending some related regulations.

- Act No. 262/2006 Coll. labor code, as amended, and some other related laws.

- Act No. 309/2006 Coll., establishing further requirements for health and safety at work in employment relationship and on ensuring the safety and protection of health during the activity or provision of services outside of the employment  relationship (Act on other occupational health and safety conditions ).

- Government Decree No. 591/2006 Coll., on detailed minimum requirements for safety and health at work on construction sites.

- Government Decree No. 272/2011 Coll., on health protection against adverse effects of noise and vibrations.

- Government Decree No. 361/2007 Coll. laying down the conditions for the protection of health at work.

- Government Regulation No. 375/2017 Coll., on the appearance, location and design of safety signs and markings and signal definition.

- Government Decree No. 495/2001 Coll. laying down the scope and detailed conditions for the provision of personal protective equipment, washing, cleaning and disinfecting means.

Earth work and excavation work, carried out in close proximity to underground electrical utilities, must be carried out only manually. Work with machinery must be adapted to the applicable safety regulations and regulations, especially in the vicinity of live electrical equipment.

The demolition must be carried out so that that the stability of the building or other structures in the immediate vicinity and the operability of the utility networks in proximity of the demolition work is not compromised, work shall be performed according to a prearranged detailed technological procedure, taking into account the survey of the actual state of construction in accordance with the MMR Decree No. 499/2006 Coll., including all other related and subsequent amendments to laws, decrees, or implementing regulations.

Worker safety

Further, the WORK shall be designed to:

- secure the equipment against accidental undesirable interference,

- equipment with potential hazardous gases presence must allow flushing with sufficient quantity of air or an inert medium.

- all rotating parts (such as pump couplings) and hot surfaces (above 50 °C) within the operator's reach must be provided with covers that will not allow touch or tangling of the operator,

- in spaces where chemicals are used or where leakage of chemicals may occur in some parts of the installation, safety showers with eye flushing (according to type operation) must be installed,

- escape routes required by fire regulations must be marked in all spaces.

At the same time, the related requirements provided in Amendment D01 of Supplement 1 to this CONTRACT must be respected

# Tests and commissioning

## General

The CONTRACTOR shall prove and demonstrate the required performance and quality of the WORK by inspections and tests that shall be carried out by the CONTRACTOR, its SUB-CONTRACTORS, at the manufacturer's premises or at the CONSTRUCTION SITE.

These inspections and tests shall include in particular:

Inspections and tests for acceptance of material and sub-deliveries of mass-produced equipment.

Inspections and tests during production of individually manufactured equipment.

Inspections and tests of finished products – FAT  Factory acceptance tests.

Inspections and tests of the civil part.

Inspections and tests at acceptance for assembly.

Individual tests (IZ) during at mechanical completion.

Inspections and tests during commissioning i.e.:

• Preparation for complex testing.

• Complex testing, TEST "A".

• Performance test.

TEST "B" (prior to  FINAL ACCEPTANCE of the WORK).

All inspections, tests and trials performed in connection with the preparation and implementation of the WORK shall be conducted in accordance with the Inspection and test plan, Test program, Commissioning plan, Guaranteed parameter test plan and other related quality documentation prepared by the CONTRACTOR in accordance with the CONTRACT, Section 27 of the CONTRACT and  Supplement 3 to the CONTRACT.

Concurrently, other conditions of the CONTRACT relevant to the testing shall be complied with, encompassed in particular in:

Section 27 of the CONTRACT - Ensuring the quality of the WORK

Section 28 of the CONTRACT - Execution and mechanical completion

Section 29 of the CONTRACT - Commissioning

Section 32 of the CONTRACT – Guarantee measurements under TEST "B", Final Acceptance of the WORK

The scope, execution and quality of the tests shall at least correspond to the requirements specified in the relevant standard for the equipment concerned. The number of the relevant and valid standard shall be provided in the accompanying documentation of the relevant tested equipment.

If the equipment shall be tested according to standards other than ČSN, these standards shall be submitted by the CONTRACTOR before the tests start.

## Inspections and tests for the acceptance of material and sub-deliveries of mass-produced equipment

These are inspections and tests at the acceptance of material and mass-produced equipment performed by CONTRACTOR´S procurement according to the approved procedures specified in the Plan of inspections and tests for acceptance of material and subcontracted deliveries, related test programs, technical conditions, and others.

The acceptance procedures shall include verification of material data sheets and certificates of the purchased material and equipment demonstrating compliance of these materials and equipment with specifications, standards and regulations, and further the quality and method of packaging and storage of individual parts of the equipment.

Records generated in connection with SUBCONTRACTOR assessment and procurement are considered to be quality records. These include, in particular, reports from external audits, records of inspections performed by the PURCHASER, protocols on equipment acceptance at SUBCONTRACTORS, inspection and test reports.

## Inspections and tests during production of individually manufactured equipment

- These are workshop tests and inspections carried out by CONTRACTOR, its SUB-CONTRACTOR, or possibly the manufacturer of the equipment in the various production stages of production according to the Inspection and test plan for the manufacture of the relevant equipment and the follow up test programs.

- Inspections and tests during manufacturing include in particular:

Material tests including material certificates.

Semi-product certificates.

Dimensional certificates, tolerances.

Inter-operational dimensional checks.

Functional tests to check the functionality of the individual parts (where possible).

Dynamic testing of rotary machines.

SKŘ component tests.

Electrical equipment tests.

Prescribed tightness tests.

Weld quality inspections.

## Inspections and tests of finished products - FAT

Inspections and tests of finished products are factory tests that are performed at the manufacturer after completion of the production and assembly of the equipment prior to its shipping in accordance with the Inspection and test plan of finished products and FAT and the follow-up test programs.

At the conclusion of these tests, before delivering the equipment to the CONSTRUCTION SITE the CONTRACTOR shall perform the Factory Acceptance Test (FAT) to demonstrate the functionality of the equipment (where possible) and its compliance with standards and specifications.

Before starting FAT, the equipment shall be fully tested by the manufacturer and all component and device errors shall be removed.

- Within FAT, all the inspections, tests and proofs required to verify the quality of finished products shall be carried out, in particular:

Complete inspection of the equipment according to the approved drawing documentation.

Quality assurance protocols review.

Pressure tests at the manufacturer.

Parameter testing of rotary machines (Q-p diagram, loading characteristics, etc.)

Checks of material tests execution,  including material certificates.

Dimension check.

Prescribed quality assurance tests of rubberized surfaces installation.

Type tests to confirm the fulfillment of design criteria for each product type. The type test may be replaced by a submission of a test report by an independent testing body and the complete documentation of the tests and their results, on which the report was based.

Functional testing of complete equipment (where possible). For modular devices and SW-containing devices these are integration tests of complete assemblies including SW.

Paint coat inspections.

Other necessary tests and proofs the CONTRACTOR shall use to demonstrate compliance of the equipment with the standards and design criteria specified in the CONTRACT.

## Inspections and tests of the civil part

For the civil part, the CONTRACTOR shall carry out inspections and tests to verify the building readiness for the follow-up construction activities or for the installation of parts or assemblies of technological devices and technical equipment. The quality management shall be in accordance with ČSN ISO 10005. The CONTRACTOR shall verify by inspections and tests carried out under the civil part Inspection and test plan (see CONTRACT Supplement 03 - Documentation) and the follow-up test programs in particular:

Shape accuracy;

Completeness and quality of execution;

Complying strength characteristics;

Compliance with the DESIGN.

Inspection and test plan

The CONTRACTOR shall prepare a pre-construction preparation schedule, including time planning and production preparation - creation of operational plans, updating of time schedules according to the actual work performed, including project control.

The CONTRACTOR shall use modern IT resources and specialized SW solutions to create a construction model with maximum integration of derived processes.

The CONTRACTOR shall provide tests especially for the following structures and technological stages:

Compaction of embankments and structures;

Piling work and geometric accuracy of piles;

Adjustment of foundation plane;

Concrete casting of reservoirs, foundations, sills and other foundation structures;

Tightness tests and waterproofing or liner barriers;

Vertical bearing structures;

Horizontal bearing structures;

Vertical access structures (elevator shafts, stairways);

Infill structures;

Steel structures;

Inspection of roofs and perimeter skin;

Inspection of dividing structure execution;

Inspection and testing of TZB equipment and distribution systems;

Inspection of finishing works execution;

Components supplied shall be accompanied by certificates of conformity.

This inventory is incomplete, the CONTRACTOR must ensure that the inspections carried out are in accordance with the valid legislation of the Czech Republic and the technical standards (ČSN, EN) as amended.

## Inspection and tests at acceptance for assembly

Inspections and tests at acceptance for assembly are tests or inspections to verify the correctness, completeness and technical state of the machines and equipment handed over for assembly and their accompanying technical documentation, and to check whether the equipment has suffered defects during transportation to the construction site, potentially preventing its proper and reliable function. These tests shall be carried out in accordance with the Inspection and test plan at acceptance for assembly and the follow-up test programs.

## Individual tests (IZ) at mechanical completion

During MECHANICAL COMPLETION, individual tests shall be carried out in accordance with the Inspection and test plan for assembly completion and according to the follow-up test programs, proving quality of the mechanical completion and the readiness of the equipment to be gradually COMMISSIONED.

These tests shall be performed on individual machines or devices separately and without loading. The intact and complete state of the supplied machinery and equipment after assembly shall be tested, the quality of the mechanical completion and the reliable operation of the individual equipment shall be proven, pressure tests and tightness tests shall be performed, and verification that cable connections are functional and properly connected, including checking the direction of movement and status signaling.

Before starting the individual tests, an initial inspection report of the electrical equipment for the entire WORK must be prepared in accordance with ČSN 33 1500 and ČSN 33 2000-6-61 as well as for the other restricted technical equipment according to the relevant valid standards and regulations. Appropriate consultations and cooperation with ITI (Institute of Technical Inspection) and OIP (Regional Labor Inspectorate).

These tests shall include in particular:

Confirmation that the CONTRACTOR has provided GOODS, SERVICES, documents and certificates in accordance with the CONTRACT as necessary for the proper operation of the facility.

Physical inspection proving that the equipment is in compliance with the final version of the drawings, the specifications and the latest applicable standards and regulations.

Inspection of  the marking on equipment,  instruments, cables, terminals, etc.

Confirmation that all pipe components within the CONTRACTOR'S supply boundaries are cleaned and flushed to allow operation without clogging or damage to the equipment.

Mechanical and hydraulic testing of all piping components and vessels within the CONTRACTOR'S supply boundaries to demonstrate their tightness and that they are clear for operation.

Testing of cable connections.

Testing of all individual machinery, measuring and control devices, automation systems, electrical equipment, lifting and handling equipment, including auxiliary equipment, so that they are treated, adjusted, calibrated and ready for normal operation.

Testing of all shut-off, protective and emergency systems for proper operation at set values.

All co-ordination activities among the other parties participating in the tests shall be provided by the CONTRACTOR.

## Inspections and tests during commissioning

Inspections and tests during COMMISSIONING shall include:

Preparation for complex testing.

Complex testing, TEST "A".

Performance test.

- These tests shall be conducted in accordance with the Inspection and test plan for commissioning and the follow-up Test program and  the Commissioning plan.

### Preparation for complex testing

Preparation for COMPLEX TESTING means the inspections and tests carried out to gradually put into operation the equipment of the individual functional units, operation systems and finally the entire WORK.

During these inspections and tests, the verification of functionality of the entire set of equipment supplied within the WORK scope, including mutual functional alignment of these devices and alignment with downstream devices and networks, is performed.

The scale of activation of the technological process in these tests depends on the nature of the particular test and shall be described in the test conditions in the test program.

These tests include in particular:

Testing functions of all machinery, measuring and control devices, automation systems, electrical equipment, lifting and handling equipment, including auxiliary equipment, so as to guarantee the complete functionality of the entire WORK and its readiness for COMPLEX TESTING including verification of the WORK connectivity to the downstream devices and its compatibility with these devices.

- These tests shall also include:

Testing of backup functions and blocking using fault simulation; for all equipment/units (process nodes, SKŘ components or electrical equipment) concerned; automatic backup and operation of the backup device/unit shall be tested and demonstrated, and the correct and timely display of the respective fault message.

Testing of all shut-off, protective and emergency systems for proper operation at set values.

Secondary tests of 6 kV substation protection.

### Complex test, test "A"

For the COMPLEX TESTING, the WORK shall be activated and operated with the respective media.

Technology, electrical equipment, control and management systems shall be fully operational, adjusted, optimized and tested together to function properly in synergy and in conjunction with the downstream equipment.

The COMPLEX TESTING shall also include inspections and tests performed under TEST "A"  including:

#### Tests performed by contractor

- These tests shall  be carried out by the CONTRACTOR according to its Inspection and test plan, Test program and in accordance with the Commissioning plan (see Supplement 3 of the CONTRACT) and shall include in particular the following inspections and tests:

- By performing TEST "A", the CONTRACTOR shall, inter alia, demonstrate that:

The supplied WORK meets, in accordance with the CONTRACT, the requirements for start-up, shut down, normal operation, fault condition resolution, etc.

Additional requirements for the technical design of the WORK provided in this CONTRACT Supplement 1, in particular the requirements for functions, technical parameters, performance, reliability, execution and quality of the WORK, are fulfilled.

All other tests provided in CONTRACT Supplement 2, not part of the GUARANTEE MEASUREMENTS,  shall be carried out.

All backup devices and automatic backups between master and backup devices are functional.

The WORK is suitable and ready to start and successfully perform the GUARANTEE MEASUREMENTS.

#### Guarantee measurements

GUARANTEE MEASUREMENTS (TEST "A") includes measurements by which the PURCHASER verifies that the WORK fulfills the guaranteed parameters specified in Supplement 2 to the CONTRACT, whose verification is required by TEST  "A".

GUARANTEE MEASUREMENTS shall be carried out by an independent third party, as determined by the PURCHASER with the participation of representatives of the CONTRACTOR.

GUARANTEE MEASUREMENTS shall be made in accordance with the Plan of GUARANTEE MEASUREMENTS prepared by CONTRACTOR and approved by the PURCHASER in accordance with the requirements of Supplement 3 to the CONTRACT.

Minor deviations in the operating conditions on the PURCHASER’S side are not a reason for not performing the "A" TEST and shall be evaluated with respect to the guaranteed correction curves that shall be part of the Plan for GUARANTEE MEASUREMENTS.

These guaranteed correction curves determine the impact on the GUARANTEED PARAMETERS Of the WORK (e.g. reagent consumption, electrical energy and SO2 removal efficiency), at different combinations of input conditions, in particular:

change in input SO2 concentration;

using a certain number of recirculation pumps and the respective nozzles used in operation;

at different flue gas volumes;

at different reactivity of limestone,

The input conditions shall be provided in the guaranteed correction curves ranging from 0 to 110% of the maximum values and further define the operating range.

If all the verification tests prescribed for these GUARANTEE MEASUREMENTS cannot be carried out for reasons not attributable to the CONTRACTOR (e.g. due to unsuitable meteorological conditions), these tests shall be made later in the TRIAL OPERATION, by agreement of the parties.

### Performance test

The COMMISSIONING shall be concluded by a performance test. The basic condition for performing the PERFORMANCE TEST shall be the successful completion of the complex testing and the signing of the completion protocol according to paragraph 29.3 of the CONTRACT.

PERFORMANCE TEST means a continuous, faultless operation of the WORK in duration according to paragraph 29.3 of the CONTRACT under all WORK operating modes.

By the PERFORMANCE TEST the CONTRACTOR proves the operability, reliability, safety and quality of the WORK in accordance with the CONTRACT in the scope and execution specified in the approved Inspection and test plan and in the approved PERFORMANCE TEST program. The CONTRACTOR has an obligation to ensure that the WORK is operated during the PERFORMANCE TEST without any maintenance interventions.

The test shall be carried out by the CONTRACTOR according to its Commissioning plan in accordance with the requirements of Supplement 3 of the CONTRACT.

## Test „B“

During the twenty-four (24) months of the WARRANTY PERIOD, on a date set by the PURCHASER, selected tests and inspections shall be performed to re-verify that the PURCHASER’S technical requirements have been met in compliance with the CONTRACT.

These tests shall include:

### Tests performed by the contractor

These tests shall be performed by the CONTRACTOR according to its Inspection and test plan, Testing programs (see Supplement 3 to the CONTRACT), with particular tests being carried out on equipment where operating difficulties and deficiencies have occurred during the previous period. In this case, they will be comparable to the tests performed in TEST "A".

In addition, tests of properties and parameters of the WORK that may deteriorate during the WARRANTY PERIOD shall be performed.

### Guarantee  measurements

GUARANTEE MEASUREMENTS (TEST "B") includes measurements by which the PURCHASER verifies that the WORK meets the guaranteed parameters specified in Supplement 2 to the CONTRACT, whose verification is prescribed in TEST "B".

GUARANTEE MEASUREMENTS shall be carried out by a PURCHASER authorized independent company or person, with the participation of representatives of the CONTRACTOR.

GUARANTEE MEASUREMENTS shall be made in accordance with the GUARANTEE MEASUREMENT plan prepared by the CONTRACTOR and approved by the PURCHASER in accordance with the requirements of Supplement 3 to the CONTRACT.

# Documentation provided by contractor

The requirements for documentation to be provided by the CONTRACTOR as part of the performance of the WORK are provided in Supplement 3 to the CONTRACT - Documentation.

# Used standards and legal and other regulations

## General

- The CONTRACTOR undertakes to observe hereinbelow in the following order:

Valid generally binding legal regulations in force in the Czech Republic, and also

Applicable harmonized standards ČSN EN i.e. standards relating to the WORK, fully transposing the requirements laid down in an European standard or a harmonization document recognized by the European Community institutions as a harmonized European standard or a European standard which has been established as a harmonized European standard in accordance with the law of the European Communities by a common agreement of the notified bodies, and also

ČSN Standards provided in Supplement 1 of the CONTRACT.

The use of foreign international or national standards is possible only if their requirements and demands are the same or stricter than those in force in the Czech Republic, subject to the prior approval of the PURCHASER. In the event that the CONTRACTOR uses a foreign standard that has no equivalent in CSN EN/ČSN, it shall submit such a standard to the PURCHASER in English with a translation into Czech, together with the documentation for approval, unless otherwise agreed by the parties.

The CONTRACTOR shall be obliged to submit to the PURCHASER, in connection with proving compliance with the requirements of the generally binding legal regulations, the required standards and the requirements of the WORK quality assurance program, the relevant documents according to this provision no later than ten (10) days prior to the commencement of the COMPLEX TEST according to paragraph 29.2 of the CONTRACT, unless the CONTRACT requires an earlier term or unless otherwise agreed by the parties.

## Requirement for compliance of the work and its execution with technical standards

The CONTRACTOR is required to comply with European and national standards and regulations unless otherwise specified in the project tender documentation specifications.

Hierarchy of standards and regulations:

Czech technical standards transposing European standards;

European standards;

European technical approvals;

Technical specifications published in the Official Journal of the European Union;

Czech technical standards;

Construction technical certificates.

Technical specifications contained in other publicly available documents commonly used in professional technical practice.

## Requirements for work implementation compliance with Purchaser´s internal management documentation

When implementing the work, the CONTRACTOR must comply with the specific requirements for the operation of the heating plant as set out in the internal guidelines of the PURCHASER. The basic document in UE is the guideline SM-UE-1805 "Contractors' Code of Conduct". This guideline addresses the majority of subjects associated with the movement and activities of contractors – external persons in UE (see Annex 11 of the CONTRACT).

# Construction site information

## Construction site preparation and drainage

The entire CONSTRUCTION SITE is located within the existing industrial site of United Energy, a.s.

Prior to the construction work, the CONTRACTOR shall build in the southern part of the CONSTRUCTION SITE the CONSTRUCTION SITE FACILITIES (ZS) including storage and parking areas (south of SO 04).

Roads

To access the CONSTRUCTION SITE, the CONTRACTOR shall use the site internal road system.

Fence

During the implementation of the WORK, the CONSTRUCTION SITE shall be fenced and equipped with entrance gates. In a visible place, an information board with the basic information on the WORK shall be installed.

Construction site drainage

Rainwater drainage from the CONSTRUCTION SITE paved staging and parking areas and from the roofs the CONSTRUCTION SITE FACILITIES shall be provided by the CONTRACTOR by installing temporary pipes connected in advance to the plant sewerage system.

## Conditions for environmental protection during construction, felling of trees

As a part of the CONSTRUCTION SITE preparation, the CONTRACTOR shall perform work on water stream, protection and designation of the existing utility networks and the transfer of the main delineation survey points of the WORK, including their protection and fixation in the field.

In all these activities, the CONTRACTOR shall act with maximum environmental care by choosing suitable equipment, providing a washing station for transport and export of soil from the CONSTRUCTION SITE and cleaning the roads.

The CONSTRUCTION SITE is located in an industrial area, there are no plant growths.

## Important overground and underground utilities

All the technical utility networks on the CONSTRUCTION SITE and their protection zones in the nearby surroundings are shown in Amendment D03.

## Construction site access

Site security is required for 24 hours, seven days a week by a professional team. Collaboration with the PURCHASER’S security is possible.

## Contractor’s working hours

CONTRACTOR'S working hours are not limited by the PURCHASER, only the decisions of state and public authorities must be respected.

## Construction site facilities

- The construction site facilities shall provide space for:

Project management staff and meetings, coordination consultations, technical councils and milestone control days;

Wardrobes and sanitary facilities for own staff and those of subcontractors;

Parking areas for trucks and heavy machinery;

Storage and assembly areas, warehouses and landfills in a sufficient extent;

Gas bottle storage;

Oil storage;

Security and fire protection equipment.

## Contractor´s activity on the construction site

The CONTRACTOR shall organize its activities in such manner that the implementation of the WORK is in accordance with the approved time schedules, in the prescribed quality, minimally disturbing the surroundings, with maximum respect for the environment and finally demonstrate the required performance parameters and perfect function in the entire WORK scope.

In view of this, the construction site facilities must be partially adjustable in order to adapt as much as possible to the needs of the construction at each construction phase.

At the expense of the CONTRACTOR, at an appropriate location, a project information board shall be installed, with dimensions of minimum 5 x 3 m, where the basic project information, responsible personnel, visualization and basic construction site facility information exchange system shall be provided.

## Water and power connections to construction site facilities

For the needs of construction site facilities and construction activities on site, connection points are set for:

Power supply - connection from the existing R04KYI substation, the contractor shall set up a 3x400/230V construction site switchboard;

Water distribution system.

Note: At the time of possible complete shutdown of the Komořany Heating Plant, no electricity shall be available from the PURCHASER’S systems, the CONTRACTOR must obtain electricity from other source (mobile generator, etc.)

## Scaffolding and auxiliary structures

- Scaffolding, auxiliary and load-bearing structures shall be used in many modifications many  times and in a different manner in different stages of construction.

- In particular the following:

Fixed platforms;

Sliding platforms;

System formwork;

Stable tubular scaffolding;

Other auxiliary structures.

- General requirements:

ČSN  EN 12 811 Temporary building structures-

Part 1: Work scaffolding - Performance requirements and general design,

Part 2: Material Information

Part 3: Load tests

ČSN 73 8101: 2005 Scaffolding. Common Provisions

- Requirements for facade scaffolding:

ČSN EN 12 810 Facade segment scaffolding-

Part 1: Requirements for products and

Part 2: Special design procedures

- Mobile scaffolding requirements:

ČSN EN 1004 Mobile access and working towers - Materials, dimensions, design loads, design requirements and safety

ČSN EN 1298 Mobile access and working towers - Rules and principles for developing assembly and operating instructions

- Requirements for pipes and couplings:

ČSN EN 74 Couplings, centering pieces and bracings for working and supporting scaffolding

Part 1: Pipe couplings - Requirements and test procedures

Part 2: Special couplings - Requirements and test procedures

Part 3: Flat studs and centering spindles - Requirements and test procedures

CSN EN 39 Steel tubes for working and supporting scaffolding - Technical delivery conditions

ČSN 73 8107 Tubular scaffolding

- Requirements for temporary edge protection:

ČSN EN 13374 Temporary edge protection systems - Product specification, test methods

ČSN 73 8106 Protection and catching structures

## Use of main lifting equipment

- The lifting mechanisms shall be different at each stage of construction. They shall be used especially for vertical and horizontal load-bearing structures, steel structure assembly, roofs and stacks, especially for installation of equipment for heat management, filtration, flue gas treatment, wastewater treatment plant, WWTP, slag conveyor and slag handling. It is assumed that both stable and mobile lifting equipment shall be used.

- These will be for example:

Cargo climbing lifts;

Stationary cranes;

Mobile crane technology;

Special mobile crane technology (stack, scrubber)

## Environmental care during construction

- During the construction period, the CONTRACTOR shall ensure in particular:

Sprinkling of processes with elevated dust release, minimizing on-site storage of loose building materials and other potential dust sources;

Continuous removal of mud and deposits on roads and paved areas;

Cleaning of construction mechanisms before going out of the CONSTRUCTION SITE through a washing station;

Ensuring good technical condition of the construction mechanisms, especially in view of the possible leakage of petroleum substances;

Implementation of constant technical inspections and maintenance of construction equipment;

The CONTRACTOR shall submit for the facility operation permit the proof of the impermeability of the newly built sumps and sewerage systems;

The CONTRACTOR shall ensure the sampling of surface and groundwater at the CONSTRUCTION SITE, to be used for water quality checks at the time of WORK implementation and its operation, including chemical analyzes;

In case of leakage of petroleum or other harmful substances, remove all contaminated soil immediately and deposit in a location designated for these purposes;

The CONTRACTOR shall provide an analysis of the excavated soils and will treat this soil in accordance with the valid legislation;

The top soil layer removed during construction work shall be used to plant the site.

## Waste management

Waste arising from construction work shall be handled in accordance with Act No. 185/2001 Coll. on waste and amending certain other acts, as amended and its implementing regulations.

The CONTRACTOR shall provide space within the construction site facilities for sorting and separate collection of individual types of waste within the plant premises in accordance with the valid legislation. The waste generated during the construction and its disposal shall be recorded as appropriate.

The CONTRACTOR shall submit for the facility operation permit the specification of the types and quantities of waste generated during the construction process and shall indicate the manner of their utilization or disposal.

Waste shall be deposited by the CONTRACTOR in large-volume containers that will be secured against unwanted tampering or waste release.

Preferably, the CONTRACTOR shall ensure the recovery of the waste prior to its disposal, the material reuse will take precedence over other waste utilization. Construction waste shall be sorted by the following items: waste earth and stones, metal, mixed building waste, wood, paper, plastic, hazardous waste.

The contractor shall hand over the waste over only to persons who are certified to accept waste under the Waste Act.

The transport equipment for waste shipment shall be closed or the loading space shall be covered in order to prevent release of the transported waste. If waste is released during transport, the waste shall be removed immediately and the place shall be cleaned.

For the facility operating permit, the CONTRACTOR shall provide evidence of how the construction waste was disposed of if recovery was not possible, and the waste records from the construction activities.

# Amendments

## Amendment D01 – Zoning permit documentation

## Amendment D02 – Dispersion study

## Amendment D03 – General layout

## Amendment D04 – Technical information on existing fabric filters

## Amendment D05 – Electrical part and control systems