Supplement 2

GuAranteed parameters

The following Supplement 2 - Guaranteed Parameters shall be completed/finalized by the contractor/participant and submitted in Volume C2 of the preliminary proposal/bid (as an annex to the WORK CONTRACT) in accordance with PURCHASER´S instructions for processing of Volume C2, contained in Part 4 of the Tender Documentation.

Legend:

The failure to attain the values with this colored background in a bold line box shall be a reason for not accepting the WORK and/or for withdrawing from the CONTRACT - see Section 42.2.19 of the CONTRACT

The failure to achieve the values with this colored background shall result in a contractual penalty - see Section 42.2 of the CONTRACT.

For values without colored background, the guaranteed values are not under penalty.

Table of Contents

1	Baseline conditions	4

1.1	Environment reference values	4

1.2	Input flue gas Parameters	4

1.3	Materials, media and energies	4

1.3.1	Limestone	5

1.3.2	Lime (hydrated lime)	5

1.3.3	Raw water	5

1.3.4	Saline water	5

1.3.5	Ash	5

1.3.6	Pneumatic transport and instrument air	5

1.3.7	Pneumatic transport Air	6

2	Guaranteed parameters	6

2.1	Emitted flue gas parameters	6

2.2	Limestone consumption	7

2.3	dry hydrate route	8

2.4	Electrical energy consumption (power requirement)	8

2.5	Compressed air consumption sourced from PURCHASER	9

2.6	Energo gypsum production	11

2.7	TOTAL WATER CONSUMPTION	11

2.8	Work availability	12

2.9	Noise emissions	13

3	Guarantee correction curves	13

4	Conditions for guarantee measurements	14

5	Terms of guaranteed parameter verification and sanctions for noncompliance	14

# 1	Baseline conditions

- During verification of the guaranteed parameters, it is not allowed to change the adjustment of the process technology; the equipment shall be operated under stable automatic operation, without manual intervention.

- Data on input parameters (flue gas, limestone, lime, water, ash) are provided in Supplement 1 to the CONTRACT and are divided into guaranteed parameters (i.e. those parameters guaranteed by the PURCHASER) and indicative parameters.

## 1.1	Environment reference values

| Ambient temperature | °C | 20 |
| --- | --- | --- |
| Elevation above sea level | m a.s.l. | 260 |
| Humidity | % | 60 |

## 1.2	Input flue gas Parameters

The guaranteed values shall be demonstrated in guaranteed parameter tests, where relevant, for the following operating states:

| - Operating state: | Abbreviation | Flue gas quantity |
| --- | --- | --- |
| -  Maximum operating state | PS Max | Q wet flue gas 800,000 Nm3/h |
| -  Operating state of boiler room 1 | PS 1 | Q wet flue gas 593,416 Nm3/h |
| -  Operating state of boiler room 2 | PS 2 | Q wet flue gas 421,550 Nm3/h |
| -  Operating state of boiler room 3 | PS 3 | Q wet flue gas 203,916 Nm3/h |
| -  Operating state of boiler room 4 | PS 4 | Q wet flue gas 600,000 Nm3/h |

The reference parameters of entering flue gas (i.e. at boiler room output) for the above mentioned operating states are provided in Chapter 1.5.1, Supplement 1 to the CONTRACT and are related to normative parameters (i.e. 101,325 Pa and temperature 0 °C).

The specific operating state at which the individual guaranteed values shall be proven is provided in Chapter 2 for the individual guaranteed parameters by the abbreviation of the respective operating state.

## 1.3	Materials, media and energies

The guaranteed values shall be demonstrated in the GUARANTEED PARAMETER TESTS using the following materials, media and energies available to the PURCHASER. Regarding compressed air, the CONTRACTOR has the option of using air from the PURCHASER’S source or from a new source constructed within the WORK scope.

### 1.3.1	Limestone

- For the operation of the WORK, the following four types of limestones are assumed, from different sources:

| - Type: | Abbreviation | Source |
| --- | --- | --- |
| -  Type 1 | V1 | Lime kiln Čertovy schody |
| -  Type 2 | V2 | Lafarge Cement |
| -  Type 3 | V3 | Kotouč Štramberk |
| -  Type 4 | V4 | Lime kiln Vitošov |

- Detailed specification of the individual limestone types, including the measured and limit values of the individual constituents/indicators for each of them are provided in Chapter 1.8.1, Supplement 1 to the CONTRACT.

- The specific type of limestone used in proving the individual guaranteed values is provided in Chapter 2 for the individual guaranteed parameters and is designated by an abbreviation of the type together with information if the measured values (abbreviated as "zm") or the limit value (abbreviated as "lim") of the constituents/indicators are consideration for the given type.

### 1.3.2	Lime (hydrated lime)

For parameters see Chapter 1.8.2, Supplement 1 to the CONTRACT.

### 1.3.3	Raw water

For parameters see Chapter 1.8.4.1, Supplement 1 to the CONTRACT.

### 1.3.4	Saline water

For parameters see Chapter 1.8.4.2, Supplement 1 to the CONTRACT.

### 1.3.5	Ash

This is a dry mixture of ash LM and LF (LM – bedding material and LF – fiber filter ash) for the production of the stabilizate. For parameters see Chapter 1.8.5, Supplement 1 to the CONTRACT.

The following hourly production of ash from combustion is assumed for the individual operating states:

| Operating state | Unit | Value |
| --- | --- | --- |
| PS Max | t/h | 52.01 |
| PS 1 | t/h | 30.73 |
| PS 2 | t/h | 21.25 |
| PS 3 | t/h | 9.71 |
| PS 4 | t/h | 35.57 |

### 1.3.6	Pneumatic transport and instrument air

For parameters see Chapter 1.8.6.1, Supplement 1 to the CONTRACT.

### 1.3.7	Pneumatic transport Air

For parameters see Chapter 1.8.6.2, Supplement 1 to the CONTRACT.

# 2	Guaranteed parameters

- The CONTRACTOR guarantees to the CLIENT that the supplied WORK shall comply with the following parameters and functions:

## 2.1	Emitted flue gas parameters

- Conditions of proofing (tests):

The following guaranteed values of the emitted flue gas must be fulfilled in all operating states of the WORK, from minimum to maximum of flue gas flow rate entering the desulphurization and in full extent of their parameters according to Chapter 1.5.1, Supplement 1 to the CONTRACT

the guaranteed values of outgoing flue gas must be met in all operating states with dynamic changes in boiler output

The following guaranteed values of emitted flue gases must be fulfilled concurrently when using all types of limestone and other raw materials provided in Chapter 1.8., Supplement 1 to the CONTRACT, when combined (for limestone).

Preferably, saline water must always be used.

Concurrently, the operation of boilers must not be adversely affected, i.e. e.g. by flue gas pressure increase or decrease above the current value at the supply boundary, deterioration of the boiler dynamics controllability, increase of own boiler consumption, etc.

| - Parameter |  | - Operating state | - Limestone | - Unit | - Relation-ship | - Guaranteed value | - Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1.1 | SO2 | all states | all types | mg/Nm3 R | less than or equal | 100 | Note (5) |
| 2.1.2 | TZL after absorber | all states | all types | mg/Nm3 R | less than or equal | 7 | Note (1) Note (5) |
| 2.1.3 | TZL after LF when operating to dry stack (after each boiler) | all states | all types | mg/Nm3 R | less than or equal | 7 | Note (5) |
| 2.1.4 | TZL separation efficiency in ABS | all states | all types | % | greater than or equal | 73.1 | Note (4) a Note (12) |
| 2.1.5 | HCl | all states | all types | mg/Nm3 R | less than or equal | 5 |  |
| 2.1.6 | HF | all states | all types | mg/Nm3 R | less than or equal | 3 |  |
| 2.1.7 | Emission (concentration) of droplets | all states | all types | mg/Nm3 R | less than or equal | 50 |  |
| 2.1.8 | Condition of minimum temperature at stack (outlet) | all states | all types | °C | greater than or equal | 54 | Note (3) |
| 2.1.9 | Hg | all states | all types | mg/Nm3 R | less than or equal | value at input |  |
| 2.1.10 | NOx | all states | all types | mg/Nm3 R | less than or equal | value at input |  |
| 2.1.11 | CO | all states | all types | mg/Nm3 R | less than or equal | value at input |  |

R…	Reference O2 concentration 6% at Standard (N) state parameters i.e. 101,325 Pa and 0 °C

N… Standard state parameters 101,325 Pa and 0 °C

Notes:

Note: (1) Required output TZL value must be provided (guaranteed) for the maximum input of 250 g/Nm3 R i.e. the original LF design value.

Note: (3) Emitted flue gas temperature must not adversely affect the dispersion parameters according to the dispersion study (i.e. in particular temperature below the temperature considered in RS)

Note: (4) Guaranteed TZL values after the absorber must be guaranteed at TZL after LF = 26 mg/Nm3 R.

Note: (5) Proof every half hour for the duration of the GUARANTEED PARAMETER MEASUREMENT and subsequently to be carried out in compliance with the applicable legislation.

Note: (12) This guaranteed parameter shall be demonstrated in one operating state as defined by the PURCHASER.

## 2.2	Limestone consumption

| - Parameter |  | - Operating state | - Limestone | - Unit | - Guaranteed value is less or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.2.1 | Limestone consumption | PS Max | V1 lim | kg/h | … To be inserted by participant |  |
| 2.2.2 | Same as above | PS 1 | V1 zm | kg/h | … To be inserted by participant |  |
| 2.2.3 | Same as above | PS 2 | V1 zm | kg/h | … To be inserted by participant |  |
| 2.2.4 | Same as above | PS 3 | V1 zm | kg/h | … To be inserted by participant |  |
| 2.2.5 | Same as above | PS 4 | V1 zm | kg/h | … To be inserted by participant |  |
| 2.2.6 | Same as above | PS Max | V2 zm | kg/h | … To be inserted by participant |  |

## 2.3	dry hydrate route

a) Maximum capacity of the dry hydrate transportation route

| - Parameter |  | - Operating state | - Dry hydrate | - Unit | - Guaranteed value is greater or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.3.1 | Capacity of dry hydrate transportation route | All | according to Chapter 1.3.2 | kg/h | 13,000 |  |

b)	Electric energy consumption of dry hydrate transportation route at transportation capacity of 13,000 kg/h

| - Parameter |  | - Operating state | - Dry hydrate | - Unit | - Guaranteed value is less or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.3.2 | Electric energy consumption of dry hydrate transportation route | 13,000 kg/h | according to Chapter 1.3.2 | kWh/h | … To be inserted by participant |  |

If air from a TKY source is used, it is necessary to state so in the table in chap. 2.5 (2.5.13 or 2.5.14).

## 2.4	Electrical energy consumption (power requirement)

The electrical power consumption of the WORK shall be measured during the operation of the WORK as the sum of the measured power values of all electrical appliances within the WORK (including the booster fan and electrical energy for the material transport to the mixer input and the energy for the production of compressed air, if the compressed air is produced by the equipment supplied within the WORK scope). The power consumption will be calculated from the electricity consumption of the relevant appliances for a defined time (to be determined in the GUARANTEED MEASUREMENT plan).

It does not include power consumption for aeration of existing silos, tanker unloading and regeneration of silo dust abatement equipment, and does not include the electricity consumption for the production of compressed air, if the compressed air is taken from PURCHASER’S sources and does not include electricity consumption for the transport of dry hydrate if produced from a source supplied within the WORK.

a)	Electrical energy consumption (input) at production of 0 % energo gypsum:

| - Parameter |  | - Operating state | - Limestone | - Unit | - Guaranteed value is less or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.4.1 | Electrical energy consumption | PS Max | V1 lim | kW (kWh/h) | … To be inserted by participant |  |
| 2.4.2 | Same as above | PS 1 | V1 zm | kW (kWh/h) | … To be inserted by participant |  |
| 2.4.3 | Same as above | PS 2 | V1 zm | kW (kWh/h) | … To be inserted by participant |  |
| 2.4.4 | Same as above | PS 3 | V1 zm | kW (kWh/h) | … To be inserted by participant |  |
| 2.4.5 | Same as above | PS 4 | V1 zm | kW (kWh/h) | … To be inserted by participant |  |
| 2.4.6 | Same as above | PS Max | V2 zm | kW (kWh/h) | … To be inserted by participant |  |

## 2.5	Compressed air consumption sourced from PURCHASER

If the compressed air required to operate the WORK shall be taken from the PURCHASER’S existing sources, the compressed air consumption shall be guaranteed, and its verification for the calculation of the power consumption shall be part of the guaranteed parameter measurement.

The compressed air consumption does not include consumption for aeration of existing silos and tanker unloading. Also, parameters 2.5.1 to 2.5.12 do not include the consumption for fly ash transport from the intermediate silo into the LF silos.

The consumption in parameters 2.5.13 respectively 2.5.14 represents air consumption from the PURCHASER's source is at the capacity of the dry hydrate route of 13,000 kg/h. Consumption in parameters 2.5.13 respectively 2.5.14 is no longer duplicated in consumption in parameters 2.5.1 to 2.5.12.

Compressed air consumption at production of 0 % energo gypsum:

| Parameter |  | - Operating state | - Limestone/Dry hydrate | - Unit | Guaranteed value is less or equal to | Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.5.1 | Compressed air consumption at 6 bar | PS Max | V1 lim | Nm3/h | … To be inserted by participant |  |
| 2.5.2 | Compressed air consumption at 3.5 bar | PS Max | V1 lim | Nm3/h | … To be inserted by participant |  |
| 2.5.3 | Compressed air consumption at 6 bar | PS 1 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.4 | Compressed air consumption at 3.5 bar | PS 1 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.5 | Compressed air consumption at 6 bar | PS 2 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.6 | Compressed air consumption at 3.5 bar | PS 2 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.7 | Compressed air consumption at 6 bar | PS 2 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.8 | Compressed air consumption at 3.5 bar | PS 3 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.9 | Compressed air consumption at 6 bar | PS 4 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.10 | Compressed air consumption at 3.5 bar | PS 4 | V1 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.11 | Compressed air consumption at 6 bar | PS Max | V2 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.12 | Compressed air consumption at 3.5 bar | PS Max | V2 zm | Nm3/h | … To be inserted by participant |  |
| 2.5.13 | Average hourly compressed air consumption at 6 bar for dry hydrate transport route at 13,000 kg/h | 13,000 kg/h | Dry hydrate | Nm3/h | … To be inserted by participant |  |
| 2.5.14 | Average hourly compressed air consumption at 3.5 bar for dry hydrate transport route at 13,000 kg/h | 13,000 kg/h | Dry hydrate | Nm3/h | … To be inserted by participant |  |

## 2.6	Energo gypsum production

Water in gypsum suspension 50% by weight in raw state

In the event of the production of the dewatered energo gypsum, the simultaneous shipment of stabilizate shall be ensured in a daily cycle.

a)	Water in energo gypsum suspension

| - Parameter |  | - Operating state | - Limestone | - Unit | - Guaranteed value is less or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.6.1 | Water in energo gypsum suspension | PS 1 | V1 zm | % | 50 |  |
| 2.6.2 | Water in energo gypsum suspension | PS 2 | V1 zm | % | 50 |  |
| 2.6.3 | Water in energo gypsum suspension | PS 3 | V1 zm | % | 50 |  |
| 2.6.4 | Water in energo gypsum suspension | PS 4 | V1 zm | % | 50 |  |

## 2.7	TOTAL WATER CONSUMPTION

Total water consumption shall be determined for operation when considering all mass included in the stabilizate (i.e. 0% energo gypsum production). The guaranteed value of "Total water consumption" shall be reported (corrected, adjusted) for extra water consumed in addition in the stabilizate according to the assumed formula, see Supplement 1 to the CONTRACT, Chapter 5.3.1, formula A).

Note: Consumption shall include water leaving with the energo gypsum to the stabilizate in the gypsum suspension.

| - Parameter |  | - Operating state | - Limestone | - Unit | - Guaranteed value is less or equal to | - Note |
| --- | --- | --- | --- | --- | --- | --- |
| 2.7.1 | Total water consumption | PS Max | V1 lim1 | t/h | … To be inserted by participant |  |
| 2.7.2 | Total water consumption | PS 2 | V1 zm2 | t/h | … To be inserted by participant |  |
| 2.7.3 | Total water consumption | PS Max | V2 zm | t/h | … To be inserted by participant |  |

## 2.8	Work availability

WORK availability means the time during which the WORK can operate during the evaluated period in all operating states listed in Chapter 1.5.1, Annexes 1 to the CONTRACT and using all the limestone types listed in Chapter 1.8.1, Supplement 1 to the CONTRACT.

WORK availability per year is equal to the total time over the evaluated period of one year when the WORK is either in operation or is ready for immediate start-up [h].

Proofing conditions (tests):

The availability shall be evaluated by the PURCHASER with the CONTRACTOR’S participation based on the facility's operational records for each year of operation within the WARRANTY PERIOD, starting from the DAY OF PRELIMINARY ACCEPTANCE OF THE WORK.

The availability does not include time from the moment the plant is shut down (switching the flue gas to the dry stack) due to a failure or accident of the plant until the device is started (introducing the flue gas into the absorber) or the time when the plant is unable to meet the guaranteed parameters.

Availability includes time for start-up from downtime and downtime caused:

- by external influences or by force majeure,

- by improper handling (non-compliance with operating instructions),

- by equipment failure not part of WORK scope,

- by PURCHASER’S decision or other reasons on its part.

For the 3rd year of operation, availability includes also time for start-ups from downtime and downtime due to failure of components without extended warranty.

Guaranteed values:

| - Parameter |  | - Unit | - Limit value equal to | - Guaranteed value is greater or equal to |
| --- | --- | --- | --- | --- |
| 2.8.1 | WORK availability in 1st year of operation | h | 8,136 | … To be inserted by participant |
| 2.8.2 | WORK availability in 2nd and 3rd year of operation | h | 8,256 | … To be inserted by participant |

Guaranteed value of availability must not be met at the expense of increased maintenance requirements

## 2.9	Noise emissions

The noise emission levels shall not exceed the maximum health limits stipulated in particular by the Act No. 258/2000 Coll. on public health protection, as amended, and Government Decree No. 272/2011 Coll. on health protection from adverse effects of noise and vibrations, as amended.

The exceedance of noise limits may be a reason for not accepting the WORK and/or withdrawing from the CONTRACT - see Section 44.2.12 of the CONTRACT

Limits for noise from stationary sources during operation - protected outdoor area of buildings:

day LAeq, 8h = 50 dB (A) (for the loudest 8 hours)

night LAeq, 1h = 40 dB (A) (for the loudest 1 hour)

These noise levels shall be verified at the points set by the government permitting authorities.

Indoor environment:

Indoor spaces without permanent operation 	maximum 85 dB (A), 1 m from the device

Internal roads			 			maximum 75 dB (A)

Control room						maximum 50 dB (A)

Offices, laboratories 					maximum 60 dB (A)

# 3	Guarantee correction curves

To be inserted by the participant, in the minimum scope as follows:

Effectiveness of desulphurization: Dependence of output SO2 concentration on input SO2 concentration in flue gas at the maximum flue gas flow rate and operation of all circulation pumps and operation without one circulation pump, in flue gas temperature range 130 - 180 °C.

Effectiveness of desulphurization: Dependence of output SO2 concentration on input SO2 concentration in flue gas, in the range 120,000 – 800,000 Nm3/h (wet) at SO2 input concentration range of 3,206 mg/Nm3 (dry, (R)) – 6,801 mg/Nm3 (dry, (R)). An extremity curve for input concentration of 10,300 mg/Nm3 (dry, (R)) shall be created, and for all cases the extreme state of SO2 input at 3,610 kg/h shall be indicated. The number of pumps shall be provided according to the design.

Consumption of sorbent: Dependence of consumption of sorbent V1 lim and V1 zm at different concentrations of SO2 in untreated (no desulfurization) flue gas (in the range from 3,206 mg/Nm3 (dry, (R)) – 6,801 mg/Nm3 (dry, (R)) for output SO2 concentration = 100 mg/Nm3 (dry, (R)), depending on flue gas flow rate between 120,000 and 800,000 Nm3/h (wet).

Electric power consumption: Dependence of power consumption (kWh/h) on flue gas flow rate in the range from 120,000 to 800,000 Nm3/h (wet) and temperature range 130 -180 °C. The curves shall be for SO2 input concentration range from 3,206 mg/Nm3 (dry, (R)) to 6,801 mg/Nm3 (dry, (R)).

Electric power consumption:  Electric power consumption curve (kWh/h) at input concentration of SO2 = 3,206 mg/ Nm3 (dry, (R)) always at the maximum flue gas flow rate, depending on the input temperature range 130 - 180 °C.

Electric power consumption: Electric power consumption curve (kWh/h) at input concentration of SO2 = 4,291 mg/Nm3 (dry, (R)) always at the maximum flue gas flow rate, depending on the input temperature range 130 - 180 °C.

Water consumption: Dependence of water consumption on flue gas flow rate in the range from 120,000 to 800,000 Nm3/h and flue gas temperature in the range of 130 - 180 °C. Measurement step 5 °C.

Quality of dewatered energo gypsum: Dependence of gypsum quality on flue gas flow rate from 120,000 – 800,000 Nm3/h and input SO2 concentration 3,206 mg/Nm3 (dry, (R)) – 6,801 mg/Nm3. Dependence of energo gypsum purity on limestone purity and limit limestone purity to attain the required quality of energo gypsum shall be determined. Maximum and minimum production of energo gypsum shall be indicated.

# 4	Conditions for guarantee measurements

The conditions for guaranteed parameter measurements shall be elaborated in detail by the CONTRACTOR in the Guaranteed parameter measurement plan, see Chapter 2.8, Supplement 3 to the Contract.

# 5	Terms of guaranteed parameter verification and sanctions for noncompliance

| Item. | Guaranteed parameter | To be verified in Guaranteed Parameter Measurements performed in |  | Parameter noncompliance results in: |  |
| --- | --- | --- | --- | --- | --- |
|  |  | test „A“ | test „B“ | Contractual penalty A) | Non-acceptance of WORK /withdrawal from CONTRACT |
| 2.1. | Emitted flue gas parameters | X | X | X | X |
| 2.2 | Limestone consumption | X | X | X |  |
| 2.3 | Dry hydrate route |  |  |  |  |
| 2.3a | Maximum capacity of dry hydrate transport route | X | X | X |  |
| 2.3b | Electric power consumption of dry hydrate route at maximum transport capacity of 13,000 kg/h | X | X | X |  |
| 2.4 | Electrical energy consumption | X | X | X |  |
| 2.5 | Compressed air consumption | X | X | X |  |
| 2.6 | Energo gypsum production |  |  |  |  |
| 2.6.a | -  Water in energo gypsum suspension | X B) |  |  |  |
| 2.7 | Total water consumption | X | X | X |  |
| 2.8 | WORK availability | XC) |  | X |  |
| 2.9 | Noise emissions | X | X |  | X |

Explanatory notes:

GUARANTEE MEASUREMENTS under TEST "A" shall be performed within the COMPLEX TEST.

GUARANTEE MEASUREMENTS under TEST "B" shall be made within the twenty-four (24) month WARRANTY PERIOD (at the end of the WARRANTY PERIOD), at a time set by the PURCHASER.

A) The penalty sanctions for non-compliance with guaranteed parameters are set out in the CONTRACT.

B) Water in the energo gypsum suspension is not part of the guaranteed parameter measurements, to be demonstrated by the CONTRACTOR during the COMPLEX TESTING for the preliminary acceptance certificate.

C) WORK availability shall be evaluated by the PURCHASER with CONTRACTOR’S participation based on WORK operational records for the 1st to 3rd year of operation after the PRELIMINARY ACCEPTANCE OF THE WORK.

Limit value according to Supplement 1 to the Contract, Chapter 1.8.1 (applies to all tables in Chapters 2.3 – 2.7)

Measured value according to Supplement 1 to the Contract, Chapter 1.8.1 (applies to all tables in Chapters 2.3 – 2.7)