SUPPLEMENT 3

DOCUMENTATION

Tender participants need to provide the following Supplement 3 – Documentation as part of Volume C3 of their Draft Offer / Offer (being a supplement to the Contract for Work) in compliance with the contracting authority’s instructions for the contents of Volume C3 contained in Section 4 of the Procurement Documents.

Supplement 3 is a listing of the Purchaser’s requirements on the scope and format, labeling, Purchaser approval, and other execution and handling issues related to the documentation prepared by the Contractor in relation to the Work.

CONTENTS

1.	Purpose of contract documentation	4

2.	Contract documentation	4

2.1	Administration rules	5

2.2	Documentation plan (PLTD)	5

2.3	Quality documentation	6

2.3.1	Quality plan	6

2.3.2	Inspection and test plan	7

2.3.3	Test program	8

2.3.4	Inspections and tests book	8

2.4	Documentation for execution of the project (design), incl. site facilities design	9

2.4.1	Purchaser’s specific requirements on the documentation for execution of the project	9

2.5	Documentation of work-in-progress change requests	12

2.6	Accompanying technical documentation	13

2.7	Commissioning plan	13

2.8	Guarantee measurement plan	14

2.9	Operations rules	15

2.10	Maintenance rules	16

2.11	Documentation required for trial operation clearance and construction approval	17

2.12	Documentation for training of purchaser personnel	17

2.13	Documentation of actual configuration	17

3.	Quantity, format, and language of contractor-provided documentation	18

3.1	Document quantities	18

3.2	Documentation format	19

3.2.1	Printed	19

3.2.2	Electronic	19

3.3	Documentation language	20

4.	Labeling	20

5.	Documentation approval	20

6.	Data provided by purchaser	21

7.	Documentation submission deadlines	21

# Purpose of contract documentation

The Contractor will need to provide, as part of the Contract, timely documentation in a scope, quantity, and quality sufficient to:

Obtain all approvals, consents, and statements from public authorities that current Czech legislation requires for the execution and subsequent operation of the Work

Assess the overall project for the Work, its timeline and deadlines, and its compliance with Contract requirements and the results and feedback from the legislative approval process

Coordinate the Work with other activities that may be ongoing at the Site

Ensure the quality of the Work

Execute the Work, including assembly and commissioning

Allow the Guarantee Measurement to be performed

Properly train the Purchaser’s personnel

Operate, maintain, and repair the Work

Document the final state of the completed Work

Throughout the execution of the Work, the Contractor shall maintain a database (listing) of the provided documentation. The will be kept in digital form as specified in Section 3 below and will contain, at minimum, the following:

Document / drawing number

Document / drawing name

Publication date and number of last valid version

Document / drawing status vis-à-vis the approvals process

Approval date (for approved documents)

Document author

Document type (Documentation for Execution of the Project, Quality Documentation, Site Facilities Documentation, etc.)

The Contractor shall provide the Purchaser with the current version of the electronic database every time any documentation is provided (including partial documentation and revisions).

# Contract documentation

As part of the Contract, the Contractor will need to provide, at minimum, the following documentation:

Administration Rules

Documentation Plan (PLTD)

Quality Documentation

Documentation for Execution of the Project (the Design)

Documentation for work-in-progress change requests

Technical documentation

Commissioning Plan

Guarantee Measurement Plan

Operations Rules

Maintenance Rules

Documentation required for official approval of completed Work and authorization of trial operation

Documentation for Purchaser personnel training

Documentation of actual execution of the Work

The requirements on document form and format listed below should always be upheld. Note that this document only discusses in detail those document types that are not specified elsewhere in the Contract (e.g. timetables).

All Contractor-provided documentation needs to maintain clarity and legibility and meet the requirements of applicable standards and engineering best practice.

## Administration rules

The document of Administration Rules define the binding rules for communication between the Contractor and the Purchaser and for the handling of Work-related documents.

The Administration Rules define procedures for document exchange between the Contractor and the Purchaser and for the publication, distribution, revisions, and archiving of such documents.

The Administration Rules also specify the standards of electronic communication between the Contractor’s and the Purchaser’s representatives.

The Administration Rules are to contain, at minimum:

- Initial provisions

- Purpose and scope of application

- Definitions and abbreviations

- Identification of documentation input and output points (both at the Contractor and at the Purchaser)

- Guidelines for communication and correspondence, assignment of responsibilities

- Requirements on headers for physical and electronic correspondence

- Addresses, identification, assigned representatives, and contact information of the Purchaser, Contractor, Construction Manager (TDI), Authorized Representatives, Notified Representatives, Occupational Health and Safety (OHS) Coordinator, independent Guarantee Measurement provider, and Purchaser’s Consultants

- Work public relations

- Final provisions

Supplements and annexes, e.g.:

Contractor’s organizational chart (with names) for Work project

Purchaser’s organizational chart (with names) for Work project

others

## Documentation plan (PLTD)

The Documentation Plan is a document defining the manner and procedures through which the Contractor creates Work-related documentation, the documentation approval process, and expected deadlines for the various documents.

The PLTD shall contain, at minimum:

1)	Formal documentation rules, such as:

Software used

Unified labeling system for printed documents

File name conventions for electronic documents

Subcontractor documentation labeling rules

Templates for drawing stamps

Templates for document cover and body pages

Templates for letters, protocols, forms, transcripts, reports, change sheets

Documentation distribution and archiving management guidelines, incl. version marking

Version history management

2)	List of documentation created by Contractor as specified in Sections 2.3 through 2.16 below, list to adequately specify, at minimum:

Document general contents and structure

Author (Contractor vs. Subcontractor)

Database structure (for database documents / lists)

3)	Documentation approval and handover timeline, being a basis for the Contractor’s provision of documents to the Purchaser for approval, timeline to include, at minimum:

Expected Contractor-Purchaser consultation days

Planned deadlines for receipt of Purchaser’s comments and approvals

Any other information that may be required to manage and coordinate the Contractor’s documentation process, e.g. inputs required from Subcontractors and Subcontractor deadlines

Time data is to be based on the current version of the project timeline and execution plan.

The current, updated version of the documentation exchange and approvals program is a required input to Progress Meetings held pursuant to Section 20 of the Contract.

## Quality documentation

Quality documentation shall include:

Quality Plan

Inspection and Testing Plan

Test programs

Inspections and Tests Book

### Quality plan

The Contractor must develop the Quality Plan for the Work in compliance with the Czech Standard ISO 10005 standard.

The Quality Plan will cover the entire scope of the Work and contain quality management procedures for all Work-related activities.

The Quality Plan will provide a full list of activities affecting the quality of the Work.

The Plan will further define the rights and responsibilities of quality management staff. The Plan will need to demonstrate that the requirements specified in the Contract are being managed and planned for and that compliance is being monitored. The Plan shall further define the standards applied, technical requirements and standards applicable to inspections, quality documentation types, and assigned staff and attendance at inspections.

The Quality Plan shall list in an orderly fashion how these activities are being managed throughout the various execution phases; i.e., during:

Design work (structural design)

Purchasing and negotiations for materials and subcontracting

Production

Construction and assembly

Commissioning

Trial Operation

### Inspection and test plan

The Contractor shall prepare an Inspection and Test Plan (ITP), this to contain all tests and inspections performed by the Contractor and its Subcontractors. The scope of inspections and testing is defined in Section 12 of Supplement 1 to the Contract (Purchaser’s Technical Requirements for the Work) for all phases of Work preparation and execution; the purpose of inspections and testing is to demonstrate the Work’s compliance with the Purchaser’s requirements.

The ITP shall include, but is not to be limited to:

Acceptance inspections and testing of materials and subcontracted mass-produced equipment

Production inspections and testing of custom equipment

Factory Acceptance Tests (FAT) of finished products

Inspections and testing of structural modules

Pre-installation acceptance inspections and testing of devices

Individual testing (IT) upon Mechanical Completion

Inspections and testing during Commissioning, including:

Preparation for Complex Tests

Complex Tests, including Test “A”

Performance Test

Test “B”

Inspection and Testing Plans are to be prepared for individual SO / IO / PS and ordered chronologically; they shall contain, at minimum:

Test or inspection name

System being tested or inspected

Test or inspection type (from among the types listed above)

Clear technical specification of the test or inspection

Testing / inspection methods and applicable legislation (the Test / Inspection Procedure), including evaluation criteria. Test and inspection for which a program has been prepared pursuant to Section 2.3.3 below, a detailed listing of criteria can be deferred to a later point in the program.

Manner in which results of test and/or inspections and evaluation are recorded

Space for Witness and Hold Points of the Purchaser’s acceptance inspection made by the PURCHASER / assigned third party’s acceptance inspection

Whenever the Contractor is required to invite the Purchaser’s representatives to participate in a test or inspection, this should always be indicated at the respective test or inspection.

### Test program

Test programs will be prepared only for:

FAT inspections and testing

Commissioning inspections and testing

Test “B” inspections and testing (performed by Purchaser or assigned third party)

Test Programs need to contain, at minimum:

Purpose of the test

Values to be demonstrated, parameters to be achieved

Description of test preparation and procedure, including a timetable

List of equipment, systems, and subsystems tested or inspected

Readiness requirements for functionally-related devices

Personnel requirements (incl. Purchaser’s representatives where required)

Line diagram representing the various tasks

List of documents and standards applicable to the test / inspection

Measurement and evaluation methods

Success criteria

List of all devices used in inspection / testing, incl. calibration protocols

Draft milestone protocols for progress evaluation (if used)

Draft final protocol

The scope, execution, and quality of testing and inspection work needs to meet, at minimum, requirements of the Contract and applicable standards.

Note: FAT Testing and Inspection Programs should only contain the relevant portions of the above data (i.e., omit interrelated devices and Purchaser personnel).

### Inspections and tests book

The Book of Inspections and Tests is a comprehensive set of documentation (protocols) of test, inspection, and acceptance test results for all activities listed in the ITP; the Book shall further include copies of calibration protocols for testing devices.

Inspections and testing documentation will be maintained separately for construction, machinery, electrical systems, and control systems; all documentation will be updated as the Work progresses.

## Documentation for execution of the project (design), incl. site facilities design

The Documentation for Execution of the Project (hereinafter also called DESIGN) is the documentation so defined in the Act no. 183/2006 – the Construction Act and in Supplement 13 to the Decree no. 499/2006 on Construction Documentation.

The Design includes all project documentation required for the construction permitting process, and must incorporate all conditions and requirements imposed on construction by the Czech Building Control Officen (or any other relevant public authorities and authorized stakeholders) as these are listed in the Construction Permit. (Note: Project documentation required for the construction permitting process will be prepared by a third-party contractor of the Purchaser and provided to the Contractor, as soon as an official approval (Construction Permit) is received .)

The Design must include all information and documentation required for the Work, including detailed technical design, process considerations, and interactions with any existing or under-construction Purchaser equipment.

In order to facilitate the Work and improve documentation standards and coordination, the Design shall further include a separate file, titled Comprehensive Design of the Work, containing design details relevant for each involved professional specialization; we note this file prevails over and above the requirements of the Decree 499/2006.

Principal sources for the Design include:

The Contract, including all Supplements thereto

The project documentation that is part of the Construction Permit, including the evaluation, comments, and requirements of involved official parties

Current standards in KKS equipment marking

Changes requested by the Purchaser during Design work

The Design is to be a comprehensive, unified whole prepared by the Contractor, and will need to consistently include data and documentation relating to any Subcontractors.

### Purchaser’s specific requirements on the documentation for execution of the project

#### Comprehensive design of the work

The Comprehensive Design of the Work is additional documentation that will need to include technical reports, drawings, calculations, and lists documenting the design of the Work as a whole across all professional specializations, including any and all relationships among different SO, IO, and PS, as well as all other documents and databases required to coordinate the Work as a whole – be they internal (among the Work’s individual SO, IO, and PS) or external (between the Work and any related structured or devices).

The Comprehensive Design thus principally summarizes the Work’s design across all professional specializations, the technologies used, how the Work breaks down into the various IO, SO, and PS, etc., including:

Overall design and layout of the Work

Design of internal and external information systems and proposed markings, advertising, etc.

Technical design of the Work as a whole, incl. all related calculations, technical and financial performance projections, coordinated master lists, etc.

Overall design of the Work’s control system, regardless of whether or not a control system element is part of a technical PS. This includes an overall configuration schematic, communication technologies used, design of electrical system connections, interface and control design, control room design and control element ergonomics, coordinated lists of measurements and signals, etc.

Overall design of the Work’s electrical systems, regardless of whether or not an electrical element is part of a technical PS.

#### Sources for ohs plan

The Contractor shall prepare a draft Occupational Health and Safety Plan for work at the Site in accordance with the requirements of the Act No. 309/2006 – the Occupational Health and Safety Act (OHSA) and of Czech Government Order no. 591/2006 on Minimum OHS Requirements at Construction Sites.

The OHS plan for the Site will need to detail the measures and standards applied to ensure adequate OHS protection and accident prevention during the Work.

The Plan will take into account the specific conditions at the Site and the specific technological processes and work activities that the Contractor will employ to realize the Work, and will complement in particular the Construction Organization Rules document.

The OHS Plan will include the Contractor’s obligation to inform the Purchaser whenever procedures and materials are used that present an increased risk to the Purchaser’s assets and / or to the life and limb of any and all natural persons that may be affected by such, considering the physical, chemical, and / or bio-active effects of these procedures and / or materials.

The Contractor shall provide the Purchaser with information on the physical, chemical, and / or bio-active effects of procedures and materials used to an extent reflecting the scientific and technological state of the art as of the time the procedure or material is used, including a listing of any preventive measures taken or available to protect the life and limb of individuals present at and around the Site.

If chemicals are used that possess at least one of the “dangerous properties” defined in the Act No. 356/2003 – the Chemicals Act, as amended, the Contractor shall be required, before commencing work, to present to the Purchaser’s representatives (or the appointed OHS Coordinator) a Czech-language Material Safety Data Sheet (MSDS) for any such chemicals.

#### Site facilities design

The Site Facilities Design document needs to include the design specification of:

Delivery unloading points

Pre-assembly and assembly areas and related machinery

Power sources and distribution on the Site

Warehouses and storage areas

Restrooms and other personnel areas

Assembly machinery, incl. manner of installation

Connection points to existing systems

Lighting

Fences, walls, etc., and security

A graphical plan of Site Facilities will also need to be provided.

The plan should be executed in 1:500 scale and contain, at minimum:

Location and elevation of all existing underground utility networks and other concealed systems

Perimeter line of the completed Work and temporary perimeter line of the Site (if outside permanent perimeter)

Location and elevation of proposed construction, including connections to Purchaser’s existing systems, as well as proposed relocations of above- or underground utility networks, if any

Areas available for storage dumps and temporary Site Facility structures

Personnel and vehicle entry points of main and secondary Site

Location of water and energy connections supplying the Site, incl. connection points; sewage connection points for Site Facilities; water drainage design, telephone connections

#### Updates to construction management rules (zov/cm)

The Purchaser shall update the Construction Management Rules (ZOV/CM) based on the CM version prepared for the construction permitting process; updates need to reflect the Timetable and Execution Plan for the Work and take into account the specific conditions at the Site, and the design and construction process proposed for the Work.

The updates need to address the basic issues in Site Facilities construction; the construction process; impact of construction on ongoing operations, the general area, and the environment; public health and safety; internal and external construction-related transportation; temporary use of land; and other elements that may impact the execution of the Work.

#### Documentation of functional systems and subsystems

Documentation of Functional Systems and Functional Subsystems (i.e., Section C of the Design) shall contain, over and above the requirements of Supplement 13 to the Decree 499/2006 on Construction Documentation, at minimum:

In Technical Report:

Any departures in the Design from the design authorized by the Construction Permit

Compliance with conditions imposed by the Construction Permit

List of applicable CSN (Czech national), CSN EN (EU, local implementation), IEC, or other standards, as currently in effect

In drawing section:

The drawing documentation of Functional (Sub)Systems should contain, depending on the purpose of the (sub)system in question: technical schematics, layout schematics of individual systems (machinery, electrical, control), cable run diagrams, dimensions, single-pole wiring schematics, grounding and electrocution protection schematics, other protection systems’ schematics, internal and external wiring schematics for all terminals in all switchboards, cabinets, and special systems, P&I diagrams incl. measurement points, control system master configuration diagram, control panel / board surface designs, workstation layouts, control system power supply schematics, control system logic schematics, line wiring schematics, terminal schematics, location labels, switchboard plans, throttling system drawings, cabling schematics, assembly drawings, etc.

In list section:

Lists should include lists of machinery and equipment, of pipe runs, valves (incl. regulation valves), and fittings, of electrical equipment, electrical network loads, measurement circuits, active elements, automation station inputs and outputs, cables, etc.

In calculations section:

Calculations should be provided in the scope and extent required and in re-checkable form.

Calculations should include calculations for steel frameworks, pressure elements, balance calculations, mechanical strength analyses, reliability calculations, regulation valve and throttle element (diaphragms, nozzles) calculations, energy consumption, waste heat production, voltage and short-circuit ratios, cable bandwidth use, etc.

All documentation sections need to be cross-referenced (incl. cross-linked if possible) to facilitate user orientation and efficient use.

Czech legislation mandates that calculations for steel frameworks, pressure systems, safety systems, etc. need to be performed by an Authorized or Notified Expert, as defined by said legislation.

#### Documentation

Documentation produced during Design work needs to be provided to the Purchaser, including, but not limited to:

Overview of maps and geodesic surveys used

Documents produced during Design work (e.g. authorized exceptions from CSN standards, compliance certificates, etc.)

List of dedicated equipment

Transcripts of design consultations, any other material documents arising from the Design process, etc.

#### KKS marking registry

The KKS Marking Registry is a list of all assigned KKS rules, including system name and numbers of drawings relating to the system.

#### List of replacement and rapid-wear parts for two years of operation post-warranty

As part of the Documentation for Execution of the Project (the Design), and pursuant to Subsection 35.3 of the Contract, the Contractor will provide a list of replacement and rapid-wear parts required for two years of post-warranty operation; to be included as Supplement 12 to the Contract.

Such parts are not included in the Contract Price, and the Purchaser reserves the right to order such parts as the Purchaser sees fit.

The list should contain all information required to identify the part in question, as well as information on recommended replacement frequency for rapid-wear parts; at minimum, this includes:

Part (material) identification

Manufacturer

Quantity

Shipping time

Identification data

Replacement frequency

Mean time to repair (MTTR)

## Documentation of work-in-progress change requests

Once Documentation for Execution of the Project (the Design) has been finalized, the Contractor shall prepare, and provide to the Purchaser, all documentation required to process requests for changes to in-progress construction and to obtain all official approvals necessitated by potential differences between the Design as executed and the preliminary design as approved in the construction permitting process (if any), or changes and approvals made and requested pursuant to the Construction Act (Act No. 183/2006) and the various Decrees implementing that Act (in particular, Decree 499/2006).

If required by the changes made, documentation shall also include a revised Building Fire Safety Design (BFSD).

Note: The Purchaser requests that, when drafting revised BFSDs, the Contractor not assume that a Corporate Fire Brigade (FB) will be present at the Site once the Work is operational, despite the fact that the Site currently has one.

## Accompanying technical documentation

All Work-related deliveries, including structural elements, need to be accompanied by any and all technical documentation required for transport, assembly, commissioning, operations, troubleshooting, and safe use.

This documentation is to include, but not be limited to:

Identification information for parts supplied

Storage requirements

Complete and approved technical data sheets and other documents required of the Contractor by Czech legislation and standards

Assembly documentation – all available manufacturer technical guidance for (dis)assembly, incl. drawings and diagrams

Passports for all pressure vessels

Passports for all pumps

Passports for the diesel generator and related equipment

Passports for lifting systems

Technical requirements on shipping, assembly, and operation

Operations, repair, and maintenance manuals

Material documentation

Certificates, MSDS, quality documents, Declaration of Conformity as required by the Act No. 22/1997 – the Product Technical Requirements Act, as amended and including all related and implementing legislation

Manufacturer’s wiring schematics for electrical systems (switchboards, control boards, cabinets, etc.)

… and others

Documentation shall be provided sorted in separate files based on whether it relates to buildings and structures, machinery, control systems, or electrical systems.

## Commissioning plan

The Commissioning Plan is a document relating to the period between Mechanical Completion and first operation; i.e., including the Complex Tests preparation period, Complex Tests, and the Performance Test.

The Plan needs to include functional tests, including preparations, and describe test conditions, media, temporary measures, and procedure, as well as required results.

The Plan shall include, but not be limited to:

Specification of default equipment parameters required for first operation

Updates to the Inspection and Testing Plan reflecting the period between Mechanical Completion and Complex Tests and related test programs

Special cleaning operations for pipe runs – this mainly involves flushing, conservation, etc.

Readiness requirements on:

Buildings and structures

Related technology

Electrical devices

Control system

First operation procedure incl. preparations

List of operating masses and energies required for first operation

Personnel requirements for first operation, by system

Line diagram showing individual activities, incl. time requirements and interactions between personnel of different specialization (structural, mechanical, electrical, control systems)

Operational testing program

Process calibration and optimization program

The section of the Commissioning Plan relating to the period of preparations for Complex Tests should use the relevant individual tests as a departure point, and should outline, in a logical progression, the start of operations on individual functional blocks and systems.

The Plan section relating to the period of Complex Tests should detail the sequence of tests of all Work parameters and functions.

This Plan section should also describe the manner in which Test “A” (Contractor’s testing) will be performed.

The Plan should also include concrete requirements on the Purchaser’s cooperation, incl. any relevant suppliers of the Purchaser, during functional testing (power, media, personnel, etc.), as further discussed in the Contract.

## Guarantee measurement plan

The Guarantee Measurement Plan, incl. calculations applied to guaranteed performance, measurement uncertainty, etc., needs to conform to current standards and describe Guarantee Measurements for all guaranteed parameters as specified in Supplement 2 (“Guaranteed Parameters”).

The Plan should, for individual guaranteed parameter measurements, include, but not be limited to:

List of tests and inspections to be performed, including their objectives

Standards applicable to evaluation

Measurement and evaluation methods

Description of measurement methods used

List of measurement devices used, incl. precision class and calibration curves

List of measurement points

Full set of correction curves and other correction data

List of measurement points, incl. corresponding marks in schematics

Design of Guarantee Measurement connection and measurement points

Timeline of testing and measurements

The Plan should further include drawings, including:

Schematic of measurement points (i.e., points need to be included in schematics) – in collaboration with Guarantee Measurement provider

Structural design and layout of sampling points – in collaboration with Guarantee Measurement provider

Measurement structure schematic

The Plan shall further define personnel requirements for testing and requirements on Purchaser’s (incl. Purchaser’s suppliers, where relevant) cooperation during Guarantee Measurements, in accordance with the provisions of the Contract and of Supplement 2 (“Guaranteed Parameters”) thereto.

Notes:

1) 	The Guarantee Measurement itself will be performed by an independent contractor hired (and paid) separately by the Purchaser.

2)	The Contractor should collaborate with the above-mentioned third party in preparing the Plan, so as to ensure the Plan’s completeness and factual accuracy.

## Operations rules

The Operations Rules will need to cover the Work as a whole, systems and subsystems, and individual devices, and should be written so as to enable operators to safely operate the Work and its components across the range of normal operating conditions, while also providing operators with sufficient guidance on how to proceed in non-standard situations. Guidelines on maximizing the economic efficiency of operations should also be included.

The Rules should conform to the Purchaser’s MPP template.

The Rules should include, but not be limited to:

Definitions of key terms

List of abbreviations

Concise technical description, labeling, and parameters of devices

Drawings (incl. schematics and dimensions)

Links among the various pieces of equipment and systems

Safe parameter variance ranges corresponding to normal operation

Threshold levels of non-standard operation

Threshold levels of emergency conditions (protection system settings)

Work procedures for operators

Listing of personnel responsible for operations, maintenance, and inspection of equipment

Handling procedures for equipment

Equipment and personnel safety, environmental safety (general and fire safety measures, etc.)

Pre-start procedures:

Technical operations monitoring

Preparation of pipe runs and active elements, description of initial state

Onlining of blocks, safeties, signals, and automatic control

Full list of release and blocking conditions for all devices / systems

Starting procedures for:

Cold start, incl. start after BO and GO

Hot start

Activation (manual, automatic)

Operational monitoring

Shutdown (standard, emergency)

Exact verbal description of binary control and regulation algorithms

Allowed ranges for regulated parameters

Evaluation of malfunction states, threshold value and control circuit settings

HMI operations manual for DCS operators

The Rules should also include a separate “Lubrication Plan” for all EVO devices, structured by technical system (incl. frequency of oil changes and lubricant top-ups and specifications for oils and other lubricants; note that ideally, the number of different oil and lubricant types used should be as low as possible).

## Maintenance rules

The Maintenance Rules should be the basic manual for maintenance work, replacement part sourcing, and personnel training.

The Rules should specify in detail the essential and recommended activities for BO and GO, the “Type Classification of Works”, and the “Deferrals Plan”, including replacement part requirements; the Rules should include, at minimum:

Specifications of key maintenance devices

Accessibility and interchangeability of the Work’s elements and nodes, incl. any need for lifting equipment for repair and maintenance of key systems

Technical procedures and requirements for repair and maintenance of key equipment

Description of preventive and reparative maintenance; drawings and schematics required for maintenance of the various devices

Timetables and guidelines for periodic revisions and maintenance, by device

Lists of replacement and rapid-wear parts, incl. all data required to order such parts; for rapid-wear parts, further including recommended replacement frequency

Special (dis)assembly procedures required for maintenance work

Troubleshooting and defect identification guidelines

Drawings showing areas, spaces, and access paths usable for disassembly of key systems and nodes, incl. temporary storage spaces and their maximum load capacity

For devices whose repair requires shutdown or low-power operation, the Rules should also list all device parts, including expected service life vis-à-vis planned repair (Normal or General) intervals.

Considering that control system maintenance includes maintenance on servo drives, throttles, and related electrical systems, the part of the electrical systems section of documentation relating to these systems needs to be written so as to be usable independently of the rest of the electrical systems documentation. Accordingly, these devices should also have separately-usable Operations and Maintenance Rules.

## Documentation required for trial operation clearance and construction approval

The Contractor will need to procure, assemble (if originally filed with other documentation), and hand over to the Purchaser all documents required by the Czech Building Control Office before it concedes the Trial Operation and Construction Approval of the Work (note: these are two separate approval processes); excepted are documents whose procurement and submission the Czech Building Control Office requires from the Purchaser (being the future Operator) pursuant to the Construction Permit.

The Contractor also needs to provide all other documents that may be requested by relevant public authorities either as part of the Construction Approval or Trial Operation approval process or at any later point.

## Documentation for training of purchaser personnel

The Contractor provides all training materials to the Purchaser in the Czech language. The scope of the training documentation is specified in Supplement 6 to the Contract.

Operator documentation (HMI operator’s manual) and the Operations and Maintenance Rules (see Supplement 6 to the Contract) need to be provided in advance that personnel may be trained without delays.

## Documentation of actual configuration

Once the Work has been commissioned and Trial Operation has been completed, the Contractor will need to provide the Purchaser with documentation of the Work’s actual configuration as built; scope is specified in Supplement 14 to the Contract and the Decree 499/2006.

Publication requirements on actual configuration documentation

Four (4) complete sets of actual configuration documentation, including all departures from the Design, need to be handed over (with protocol) to the Purchaser before the PAC is signed. This documentation needs to contain any and all changes made as of the time of documentation transfer. All documents need to contain the Contractor’s statement that “documentation reflects the Work’s actual configuration”, including the date, the Contractor’s stamp, and a Contractor representative’s signature. The documentation needs to also include the Situation Plan, which records the precise positions of all above- and underground utility networks and all structures (roads and buildings). The Situation Plan must meet the requirements for entry into the Czech Real Estate Registry. The Purchaser will only sign the PAC once this documentation has been provided.

Eight (8) complete sets of the final version of the actual configuration documentation, which should further include all changes made during Trial Operation, including all source files for documents created via specialized software, need to be handed over (with protocol) to the Purchaser once Trial Operation concludes. All documents need to contain the Contractor’s statement that “documentation reflects the Work’s actual configuration”, including the date, the Contractor’s stamp, and a Contractor representative’s signature.

This documentation should also include a current version of the Replacement and Rapid-Wear Parts List corresponding to two years of post-warranty operation.

# Quantity, format, and language of contractor-provided documentation

Documentation needs to have a unified and comprehensible format and conform to engineering best practice. The Contractor should ensure that any documentation provided by Subcontractors matches the format and labeling scheme of the remainder of Work documentation.

All documents handed over by the Contractor need to bear a header stamp (stamp template to be provided by the Purchaser).

No document may contain any clause that would limit the Purchaser in any way from using the documentation as intended, nor bind the Purchaser to request the Contractor’s approval for any such use (see also Subsection 17.3-a of the Contract). All documents found to contain such clauses will be returned to the Contractor for amendment.

All documents should use système international (SI) units only. Drawing scale needs to conform to applicable technical standards and best practices. All drawings need to include a scale bar. In drawings produced in a reduced size, legibility must always be maintained.

## Document quantities

All documentation discussed above should be handed over to the Purchaser only once approved, and as approved; quantities of printed identical counterparts as follows:

| Section | Documentation type | Approval draft | Final version |
| --- | --- | --- | --- |
| 2.1 | Administration Rules | 3 | 3 |
| 2.2 | Documentation Plan (PLTD) | 3 | 3 |
| 2.3 | Quality Documentation | 2 | 2 |
| 2.4 | Documentation for Execution of the Project (the Design), incl. Site Facility Design | 3 | 6 |
| 2.5 | In-progress design change request documentation | 3 | 8 |
| 2.6 | Accompanying technical documentation | 1 | 3 originals |
| 2.7 | Commissioning Plan | 3 | 6 |
| 2.8 | Guarantee Measurement Plan | 3 | 6 |
| 2.9 | Operations Rules | 3 | 3 |
| 2.10 | Maintenance Rules | 3 | 3 |
| 2.11 | Construction Approval and Trial Operation approval documentation | - | 3 |
| 2.12 | Purchaser personnel training documentation | 2 | appropriate to personnel trained |
| 2.13 | Work actual configuration documentation (incl. List of Replacement and Rapid-Wear Parts and Situation Plan) | 1 | 4 + 8 (see 2.13 above) |

The same number of copies will also be provided digitally on flash drives (one copy – one drive), formatted and ordered as specified in Section 3.2.2 below.

## Documentation format

### Printed

Printed documents and drawings need to conform to CSN standards in their formatting. Text documents should be on A4 size paper; other documents should preferentially be on A4 or A3 size paper.

Large paper formats should be used for drawings; these need to foldable to a size that can be filed in an A4 size binder.

If design elements are added to existing documents, the original formatting should be preserved.

Drawing originals (master copies) should be high-quality prints (incl. paper / material) made on laser, inkjet, or plotter printers.

### Electronic

#### File format

Drawings should be in native AutoCAD Rel. 2004 or earlier format (DWG, DXF).

Text documents should be in native MS Word 2007 or later format (DOC, DOCX).

Databases, tables, and lists should be in native MS Excel 2007 or later format (XLS, XLSX).

Timetables should be in native MS Project 2007 format (MPP), with a copy in PDF format.

Graphics files (any photo documentation that may be included with technical specifications) should be in JPG format.

Scans should be in PDF format.

All electronic documents should be unlocked (i.e., not password-protected or otherwise access-restricted); the Purchaser should be able to further process (edit, copy, print, convert to other formats, etc.) all documents if required.

Documentation should be editable and no compatibility-limiting add-ons (e.g. CADELEC) should be used.

Documents not conforming to the above will be returned to the Contractor for reformatting.

Documents that the Contractor itself does not have available in editable form (e.g. data sheets, inspection reports, etc.) shall be exempted from the above.

Any and all non-standard fonts, libraries, styles (line, shading, plotting, etc.), and other elements required for proper and complete display need to be included with the electronic documentation.

#### Filing system for electronic documents

Electronic documents created as part of the Work should be handed over to the Purchaser on USB flash drives.

Flash drives should be numbered (ascending); the number needs to be indicated on the drive casing.

File names and directory structure should facilitate quick, simple, and unambiguous navigation and file identification (incl. general contents).

A directory structure with verbal directory names and comprehensible file names should therefore be used.

All media provided should contain a file (called Obsah.doc or Obsah.xls – note Obsah is Czech for “Contents”) illustrating the directory structure used and listing file names and paths, with a brief description of file contents.

## Documentation language

All documentation shall be provided in the Czech language. Drawing annotations are acceptable in English if a legend with Czech translations is provided.

The only exception allowed by the PURCHASER is for documentation of control system hardware and software and for originals of data sheets for imported goods; these may be in English (but no other foreign language).

Czech translations need to be provided for equipment certificates.

# Labeling

The Purchaser requires that equipment be labeled in the KKS rules system.

The coding scheme selected should be unified across the entire body of documentation and all equipment supplied and should be consistent with the labeling of the existing devices.

# Documentation approval

The Contractor will need to prepare and submit to the Purchaser for approval, in line with the agreed schedule, the documentation required for the Work.

The Contractor should hand over documentation as it becomes due pursuant to the timetable given in the Contract and in Section 7 below.

All documentation submitted for approval will include a cover letter listing the documents being submitted.

Any subsequent versions and revisions of previously-approved documentation should contain a list of changes from the most recent approved version. Such changes should be implemented as revisions (text documents, lists) or highlighted by bubbles (drawings).

The Purchaser shall be obligated to either return to the Contractor an approved copy or to inform the Contractor in writing that approval was not issued, including the reasons, within ten (10) business days of recorded receipt of any documentation submitted for approval. Documentation may, if so agreed between the parties, be approved by written statement only without returning a copy to the Contractor.

If the documentation submitted by the Contractor for approval, or a significant subset thereof (e.g. SO, IO, PS), is incomplete, this limits the Purchaser’s ability to properly assess the documentation; the Purchaser will, in that case, inform the Contractor to this effect without delay, and the 10-day approval period will be reset once the Purchaser has received the additional documentation / explanation of omissions. The same procedure will apply if a submission cannot be approved due to errors, contradictions, departures from the Contract, or other non-conformities being found; in this case, the Purchaser will inform the Contractor and request resolution of the issues found and subsequent re-submission.

If the Purchaser declines to issue approval for reasons consistent with the terms of the Contract, the Contractor will need to resolve the issues given by way of reason and re-submit the documentation in question. The approval process will then function as outlined above, but the Purchaser may only decline to approve re-submissions for reasons of (i) issues found in material changed from previous submissions; or (ii) issues in other (incl. previously approved) parts of the documentation that are impacted by new changes, but fail to adequately address the Purchaser’s concerns given by way of reason for the Purchaser’s previous refusal to approve the documentation.

Documentation portions to which the Purchaser had no objection (i.e., which were not a contributing factor in a refusal to approve) shall be considered “approved in principle”; i.e., the Contractor will be able to perform works based on these portions.

The Purchaser may only refuse to approve documentation for reasons of conflict with the Contract or non-conformity with engineering best practice.

The Purchaser’s approval of any documentation (whether on first submission or with changes) does not exempt the Contractor from any of its duties under the Contract, and the Contractor remains responsible for the contents of the documentation.

The deadlines for documentation submission given in the Contract apply to approved documentation. Any delays in the Work caused by the Contractor’s failure to have documentation approved within the expected timeframe are wholly the responsibility of the Contractor.

# Data provided by purchaser

Aside from data, drawings, and other documentation included in the Contract, the Contractor shall further receive a single Czech-language copy of each of the following:

Design documentation from the construction permitting process (incl. electronic copy); Construction Permit as issued, incl. any conditions and requirements imposed therewith by the Czech Building Control Office and / or other Czech public authorities

Available land and terrain surveys

Available actual condition documentation wherever the Contractor’s work will connect to existing Purchaser equipment

# Documentation submission deadlines

All documentation processed by the Contractor should be submitted to the Purchaser by the deadlines given in Subsection 10.1 of the Contract.

Purchaser-provided documentation will be handed over as follows:

| Document | handed over to Contractor |
| --- | --- |
| Design documentation for construction permitting, incl. statements from authorities | no later than upon Contract signing |
| Construction Permit and other official documents | no later than 7 days from date of legal effect |
| Actual condition documentation of existing Purchaser equipment Contractor’s work will link to (where available) | no later than 15 days from Contractor’s request |