SEZNAM POVINNÝCH TECHNOLOGIÍ

Účelem tohoto seznamu je vymezit technologie, které je nezbytné v rámci retrofitu kotlů K80 a K90 vyměnit z důvodu vypršení jejich životnosti, a naopak které je nutné zachovat. Zbytek systémů je na posouzení zhotovitele.

| technologie | stav | poznámka |
| --- | --- | --- |
| přehřívák 1.1 - závěsné tyče | vyměnit | po životnosti |
| přehřívák 1.2 - část membránové stěny | upravit | aktuální stav nutný k posouzení, navržené možnosti jsou buď výměna či dodatečná ochrana např. žáruvzdorným nástřikem odolným vůči chlorové korozi |
| přehřívák 1.3 - vodorovná část | vyměnit | po životnosti |
| přehřívák 3 | vyměnit | po životnosti |
| ekonomizér | vyměnit | po životnosti |
| potrubí výparníku ve spalovací komoře pod vyzdívkou | vyměnit | po životnosti |
| spalinovody - za spalinovým ventilátorem do komínu | ponechat | v roce 2022 byl proveden vnitřní ochranný nástřik |
| regulační a hořákové řady hořáků | vyměnit | možnost redukce počtu najížděcích hořáků, u každého kotle musí být jeden kombinovaný pro možnost spalování technologického paliva |
| 1. a 2. svazek LUVO (podle směru vzduchu) | ponechat | již byly a budou vyměněny před začátkem projektu |
| DSI | ponechat | je povolena změna sorbentu (Ca(OH)2 x NaHCO3) - obojí již testováno, kompatibilní, jsou povoleny dílčí výměny komponentů (podléhá schválení ŠE) |
| SNCR | ponechat | jsou povoleny změny v oblasti kotelny a dílčí změny ve skladu zásobování SNCR (např. navýšení výkonu čerpadel), není povolena úplná náhrada technologie stáčení, skladování a čerpání |
| tkaninové filtry | ponechat | není povolena úplná demolice filtrů, jsou povoleny změny spočívající ve výměně tkaninových rukávců, rozšíření filtrů je povolené, je povolena změna spočívající v úpravě či vestavbě systémů do stávající technologie |
| kompresory centrálního stlačeného vzduchu | ponechat/vyměnit | všechny kompresory centrálního stlačeného vzduchu budou demontovány vyjma nového kompresoru řídícího vzduchu, který bude přesunut do nové kompresorové stanice |
| vnitřní zásobníky uhlí | vyměnit | nejsou kompatibilní s řešením dřevní štěpky z důvodů klenbování |
| peletkové hospodářství | ponechat | jsou povoleny jen úpravy spočívající v zaústění dávkování peletek do kotle |
| dopravníky paliva mezi bukrem a kotlem | vyměnit | nejsou kompatibilní s řešením dřevní štěpky z důvodů častých poruch a sklonu dopravníku |
| vápencové hospodářství | ponechat | jsou povoleny úpravy při zaústění dávkování do kotle, je povoleno snížit výšku sila z důvodu snížení úrovně místnosti přijmu paliva |
| silo MFV | ponechat | jsou povelené úpravy na technologii dávkování MFV, silo je možné použít pro uskladnění a dávkování písku v případě potřeby |
| V rámci projektu není povoleno na žádném kotli spalování síry. Pro ochranu před účinky Cl preferujeme jiná opatření spočívající ve využití (NH4)2SO4 v SNCR či ochranném nástřiku teplosměnných ploch. |  |  |

LIST OF MANDATORY TECHNOLOGIES

The purpose of this list is to define the technologies that must be replaced as part of the retrofit of K80 and K90 boilers due to the end of their lifetime, and systems, which must be preserved. The rest of the systems are at the assessment of the contractor.

| technology | status | note |
| --- | --- | --- |
| superheater 1.1 - hanging rods | replace | out of lifetime |
| superheater 1.2 - part of membrane wall | modify | current condition required for assessment, possible options are replacement or additional protection, e.g. heat-resistant coating resistant to chlorine corrosion |
| superheater 1.3 – horizontal part | replace | out of lifetime |
| superheater 3 | replace | out of lifetime |
| economizer | replace | out of lifetime |
| evaporator pipe in the combustion chamber under the refractory wall | replace | out of lifetime |
| flue gas pipes - from flue gas fan to the stack | remain | in 2022, an internal protective coating was applied |
| regulation and burner lines of burners | replace | is allowed to reduce number of start-up burners, each boiler must have one combined for the possibility of burning technological fuel |
| 1. a 2. parts of air preheater (by the air way) | remain | have already been and will be replaced before the start of the project |
| DSI | remain | change of sorbent (Ca(OH)2 x NaHCO3) is allowed - both already tested and they are compatible, partial replacement of components is allowed (subject to ŠKO-ENERGO approval) |
| SNCR | remain | changes in the area of the boiler hall and partial changes in the SNCR supply warehouse are allowed (e.g. increasing the power of pumps), complete replacement of bottling, storage and pumping technology is not allowed |
| bag house filters | remain | complete demolition of filters is not allowed, changes consisting in the replacement of fabric sleeves are allowed, expansion of filters is allowed, changes in modification or integration of systems into existing technology are allowed |
| central compressed air compressors | remain/replace | all central compressed air compressors will be dismantled except for the new instrumental air compressor, which will be moved to the new compressor station |
| inner fuel silos | replace | they are not compatible with the wood chip solution due to bridging |
| pellets fuel management | remain | only modifications consisting in feeding the pellets into the boiler are allowed |
| inner fuel conveyors from silos to boilers | replace | they are not compatible with the wood chip solution due to frequent breakdowns and the inclination of the conveyors |
| limestone management | remain | modifications are allowed at the inlet of limestone to the boiler, it is allowed to reduce the height of the silo due to lowering the level of the fuel intake room |
| ash/sand silos | remain | modifications to the ash/sand dosing technology are allowed, silos will be same |
| Sulfur burning is not allowed on any boiler. For protection against the effects of Cl, we prefer other methods e.g. (NH4)2SO4 in SNCR or protective spraying of heat exchange surfaces. |  |  |