Preliminary Market Consultation – Supply of Steam Electrode Boiler
This form is used to carry out a preliminary market consultation pursuant to Section 33 of Act 134/2016 Coll., hereinafter referred to as "ZVZZ". This is not a tender procedure within the meaning of Act No. 134/2016 Coll. and does not constitute a right to conclude a contract. The Contracting Authority reserves the right to contact potential suppliers directly.
1. Identification Data of the Contracting Authority
	Name of the contracting authority
	TAMERO INVEST s.r.o.

	Company ID
	24781452

	Contact person
	Tomáš Medveď

	E-mail / phone
	verejne.zakazky@synthosgroup.com
736-527 -226

	Registered office address
	O. Wichterleho 81, 278 01 Kralupy nad Vltavou, Czech Republic


2. Subject of Delivery
Manufacture and delivery of steam electrode boiler, including accessories, commissioning, warranty tests, operator training, and accompanying technical and supplier documentation for the equipment. The supplier may offer a suitable technology subject to the parameters set out below. 
3. Required Technical Parameters
Fuel:




      6.3 kV electrical energy
Feed water:
existing feed water 105 °C 
Rated steam output:
20 t/h
Minimum output:


      5 t/h (at rated steam output parameters)
Rated output steam parameters:
      the boiler will supply steam at 1MPa 
	
	Operating pressure
	Minimum pressure
	Maximum pressure
	Operating temperature
	Minimum temperature
	Maximum temperature

	Steam 1.0 MPa
	0.850 to 0.865 MPag
	0.85 MPag
	0.90 MPag
	260 to 265 °C
	260 °C
	280 °C


Minimum efficiency:


98% 
Boiler start-up speed:


Within 5 minutes 
4. Scope of Delivery and Services
- Manufacturing, transport, supervision during installation and commissioning of the boiler  
- Warranty tests and setup reports
- Operator training
- Handover of accompanying technical/supplier documentation, including installation operating and service manuals and a list of recommended spare parts
- Warranty for a minimum of 24 months from acceptance
5. Supplier's Answers – please, fill in
	Technical parameters of boilers
	 
	 
	Note

	Dimensions W x H x D
	mm
	 
	 

	Weight
	kg
	 
	 

	Efficiency at rated output
	%
	 
	 

	Power consumption at rated output
	kWh
	 
	 

	Minimum boiler output at rated steam outlet temperature 
	t/hr
	 
	 

	Minimum boiler output at a steam outlet temperature 10 °C lower than the minimum steam temperature
	t/hr
	 
	 

	Boiler overload capacity (amount of steam above max. output)
	t/hr
	 
	 

	Time required for cold start to reach the rated output
	min
	 
	 

	Time required for warm start to reach the rated output
	min
	 
	 

	Time required to increase the minimum output to reach the maximum output
	min
	 
	 

	Time required to reduce the maximum output to reach the minimum output
	min
	 
	 

	Climatic conditions – temperature range, in which the boiler can be operated and started up
	°C
	 
	 

	
	

	Operating parameters of boilers
	Note

	Temperature control of steam output +/-5 °C from the set value
	YES / NO
	 
	 

	Automatic cold start without operator intervention, including temperature curve compliance
	YES / NO
	 
	 

	Automatic warm start without operator intervention, including temperature curve compliance
	YES / NO
	 
	 

	Automatic operation at rated output (without operator intervention)
	YES / NO
	 
	 

	Automatic operation at minimum output (without operator intervention)
	YES / NO
	 
	 

	Boiler Accessories / Other
	Note

	Feed pump with frequency converter 
	YES / NO
	 
	 

	Feed control valve 
	YES / NO
	 
	 

	Equipment required for cold start 
	YES / NO
	 
	 

	Autonomous control system for boiler operation, including pumps, valves, etc., incl. control panel located in the control cabinet – for each boiler
	YES / NO
	
	

	Electrical switchboard for boiler consumption for powering electrical accessories of a boiler/boilers and feed pumps
	YES / NO
	
	

	Transmission of all measured values from the boiler control system, including protections, to the heating plant control system
	YES / NO
	 
	 

	Transmission of information on the status of equipment (valves, pumps, etc.) to the existing heating plant control system
	YES / NO
	 
	 

	Each boiler protection is listed as a separate specific item (not as combined protection)
	YES / NO
	 
	 

	Equipment required for boiler descaling 
	YES / NO
	 
	 

	Equipment required for boiler desludging 
	YES / NO
	 
	 

	Chemical treatment of boiler water 
	YES / NO
	 
	 

	Chemical treatment of feed water 
	YES / NO
	 
	 

	Platforms and service gangways 
	YES / NO
	 
	 


Note: 
YES – it is included in the boiler delivery (in the indicative price) 
NO – it is not included in the boiler delivery 
"Empty cell" – the supplier is able to provide this according to the customer's requirements (not included in the indicative price)
	Commercial section 
	Note

	Indicative price (without VAT) for the delivery of two boilers, including accessories
	CZK
	
	 

	Delivery time from contract signing (manufacture and delivery)
	months
	 
	 

	Estimated commissioning time after installation completion (MC)
	weeks
	 
	 


7. Response Deadline and Delivery Method
Please, send the completed form no later than on 11th February 2026. Method of delivery: e‑mail. 
8. Declaration of the Contracting Authority
This document is intended solely for market research purposes. The contracting authority reserves the right to specify the parameters and scope of performance in subsequent tender documentation. The information provided by the supplier will only be used for internal evaluation.
9. Signatures
	On behalf of the contracting authority
	

	Name, position, e-mail, signature, date
	


	On behalf of the supplier
	

	Name, position, e-mail, signature, date
	


