Preliminary market consultation – Supply of 2 steam boilers

This form is used to carry out a preliminary market consultation pursuant to Section 33 of Act 134/2016 Coll., hereinafter referred to as "ZVZZ". This is not a tender procedure within the meaning of Act No. 134/2016 Coll. and does not constitute a right to conclude a contract. The Contracting Authority reserves the right to contact potential suppliers directly.

## 1. Identification Data of the Contracting Authority

| Name of the contracting authority | TAMERO INVEST s.r.o. |
| --- | --- |
| Company ID | 24781452 |
| Contact person | Tomáš Medveď |
| E-mail / phone | verejne.zakazky@synthosgroup.com +420-736-527-226 |
| Registered office address | O. Wichterleho 81, 278 01 Kralupy nad Vltavou, Czech Republic |

## 2. Subject of Delivery

Manufacture and delivery of 2 steam boilers including accessories, commissioning, warranty tests, operator training, accompanying technical and delivery documentation for the equipment. The supplier may offer a suitable technology subject to the parameters set out below.

## 3. Required Technical Parameters

Fuel: 	natural gas, homogeneous mixture of natural gas and refinery off-gas (chemical properties and calorific value identical to natural gas)

Feed water:				existing feed water 105 °C

Rated steam output:			40 t/h each

Minimum output:			15 t/h (at rated steam output parameters)

Rated steam output parameters:	the boiler will supply steam at 1MPa or 1.6MPa

|  | Operating pressure | Minimum pressure | Maximum pressure | Operating temperature | Minimum temperature | Maximum temperature |
| --- | --- | --- | --- | --- | --- | --- |
| Steam 1.0 MPa | 0.850 to 0.865 MPag | 0.85 MPag | 0.90 MPag | 260 to 265 °C | 260 °C | 280 °C |
| Steam 1.6 MPa | 1.38 MPag | 1.32 MPag | 1.42 MPag | 225 to 245 °C | 220 °C | 250 °C |

Minimum efficiency:			95% (from 40% to 100% output)

Emission requirements:		according to BAT

Boiler start-up speed:			warm start within 20 minutes

cold start within 2 hours

## 4. Scope of Delivery and Services

- Manufacturing, transport, supervision during installation and commissioning of two boilers, including accessories

- Warranty tests and setup reports

- Operator training

- Handover of the accompanying technical/supplier documentation, incl. installation, operating and service manuals and a list of recommended spare parts

- Warranty for a minimum of 24 months from acceptance

## 5. Supplier's Answers – please, fill in

| Technical parameters of boilers |  |  | Note |
| --- | --- | --- | --- |
| Dimensions W x H x D | mm |  |  |
| Weight | kg |  |  |
| Efficiency at rated output | % |  |  |
| Power consumption at rated output | kWh |  |  |
| Minimum boiler output at rated steam outlet temperature | t/hr |  |  |
| Minimum boiler output at a steam outlet temperature 10 °C lower than the rated steam temperature | t/hr |  |  |
| Boiler overload capacity (amount of steam above max. output) | t/hr |  |  |
| Time required for cold start to reach the rated output | min |  |  |
| Time required for warm start to reach the rated output | min |  |  |
| Time required to increase the minimum output to reach the maximum output | min |  |  |
| Time required to reduce the maximum output to reach the minimum output | min |  |  |
| Climatic conditions – temperature range, in which the boiler can be operated and started up | °C |  |  |

| Operating parameters of boilers |  |  | Note |
| --- | --- | --- | --- |
| Temperature control of steam output +/-5 °C from the set value | YES / NO |  |  |
| Automatic cold start without operator intervention, including temperature curve compliance | YES / NO |  |  |
| Automatic warm start without operator intervention, including temperature curve compliance | YES / NO |  |  |
| Automatic operation at rated output (without operator intervention) | YES / NO |  |  |
| Automatic operation at minimum output (without operator intervention) | YES / NO |  |  |

| Boiler accessories |  |  | Note |
| --- | --- | --- | --- |
| Automatic boiler descaling | YES / NO |  |  |
| Automatic boiler desludging | YES / NO |  |  |
| Air ducts – fan intake | YES / NO |  |  |
| Air ducts – fan discharge | YES / NO |  |  |
| Air ducts silencer | YES / NO |  |  |
| Flue gas intake piping – recirculation | YES / NO |  |  |
| Flue gas discharge piping | YES / NO |  |  |
| Feed pump with frequency converter, 2 pcs / boiler | YES / NO |  |  |
| Feed control valve, 2pcs | YES / NO |  |  |
| Feed tank 40 m3, including degassing and water control valve to feed tank / boiler | YES / NO |  |  |
| Equipment required for cold start (e.g. combustion air heating, if applicable) | YES / NO |  |  |
| Autonomous control system for boiler operation control, incl. burners, pumps, fans, valves, etc., incl. control panel located in the control cabinet – for each boiler | YES / NO |  |  |
| Electrical switchboard for boiler consumption for powering electrical accessories of a boiler/boilers and feed pumps. | YES / NO |  |  |
| Transmission of all measured values from the boiler control system, including protections, to the heating plant control system | YES / NO |  |  |
| Transmission of information on the status of equipment (valves, pumps, etc.) to the existing heating plant control system | YES / NO |  |  |
| Each boiler protection is listed as a separate specific item (not as combined protection) | YES / NO |  |  |
| Equipment required for boiler descaling | YES / NO |  |  |
| Equipment required for boiler desludging | YES / NO |  |  |
| Chimney | YES / NO |  |  |
| Chimney silencer | YES / NO |  |  |
| Chemical treatment of boiler water | YES / NO |  |  |
| Chemical treatment of feed water | YES / NO |  |  |
| Platforms and service gangways | YES / NO |  |  |
| Emissions monitoring | YES / NO |  |  |

Note:

YES – it is included in the boiler delivery (in the indicative price)

NO – it is not included in the boiler delivery

"empty cell" – the supplier is able to provide the item according to the customer's requirements (not included in the indicative price)

| Commercial section |  |  | Note |
| --- | --- | --- | --- |
| Indicative price (without VAT) for the delivery of two boilers, including accessories | CZK |  |  |
| Delivery time from contract signing (manufacture and delivery) | months |  |  |
| Estimated commissioning time after installation completion (MC) | weeks |  |  |

## 7. Response Deadline and Delivery Method

Please, send the completed form no later than on: 11th February 2026. Method of delivery: e‑mail.

## 8. Declaration of the Contracting Authority

This document is intended solely for market research purposes. The contracting authority reserves the right to specify the parameters and scope of performance in subsequent tender documentation. The information provided by the supplier will only be used for internal evaluation.

## 9. Signatures

| On behalf of the contracting authority |  |
| --- | --- |
| Name, position, e-mail, signature, date |  |

| On behalf of the supplier |  |
| --- | --- |
| Name, position, e-mail, signature, date |  |