# Annex No. 4 to the Contract for Work – Guarantee Calues

[note by contracting entity: the wording of this annex corresponds to part of Annex A 6 of the tender documentation; in the text of this annex, the numbering of paragraphs and references of annex A 6 of the tender documentation is preserved]

  - 4.5 The Boiler Efficiencies

The indirect method according to ČSN EN 12 952 will be used to determine the guaranteed efficiency.

|  | Parameter | Units | The value of the guaranteed parameter | LIMIT VALUE OF THE GUARANTEED PARAMETER |
| --- | --- | --- | --- | --- |
|  | The boiler K20 - Fuel 1 |  |  |  |
| G14.1 | The average boiler efficiency at nominal boiler output for fuel 1: wood chips | % | TO BE ADDED | min. 91 |
|  | The boilers K80 and K90 -Fuel 1 |  |  |  |
| G14.2.1 | The average boiler efficiency at the boiler nominal output for the fuel 1: wood chips - for the duration of 24 hours | % | TO BE ADDED | min. 89 |
|  | The boilers K80 and K90 for any mixture of fuel 1: wood chips – 60percent and the fuel 2: plant pellets – 40percent |  |  |  |
| G14.2.2 | The average boiler efficiency at the boiler nominal output for the fuel mixture | % | TO BE ADDED | min. 89 |

  - 4.6 Minimum Steam Output of the Boiler

It is applied to reference fuels, reference feed water temperature and reference conditions.

|  | Parameters at the connecting points | Units | Value |
| --- | --- | --- | --- |
|  | Boiler K20, fuel 1 |  |  |
| G15.1.1 | Minimum steam output of the boiler K20 at the connecting point | % | 40 |
| G15.1.2 | the K20 boiler at the minimum steam output of the boiler | °C | 520 |
| G15.1.3 | K20 steam pressure at the minimum steam output of the boiler | MPa(g) | 12 |
|  | Boilers K80 and K90, fuel 1 |  |  |
| G15.2.1 | Steam output of each of the K80 and K90 boilers at the boiler outlet for fuel 1: wood chips | % | 60 |
| G15.2.2 | Steam temperature of each of the K80 and K90 boilers at the minimum steam output for fuel 1: wood chips | °C | 520 |
| G15.2.3 | Steam pressure of each of the K80 and K90 boilers at the minimum steam output for fuel 1: wood chips | MPa(g) | 12 |
|  | Boilers K80 and K90 fuel mix based on heat input |  |  |
| G15.3.1 | Steam output of each of the K80 and K90 boilers at the boiler outlet for fuel 1: wood chips - 60% and fuel 2: plant pellets – 40% | % | 60 |
| G15.3.2 | Steam temperature of each of the K80 and K90 boilers at the minimum steam output for fuel 1: wood chips - 60% and fuel 2: plant pellets – 40% | °C | 520 |
| G15.3.3 | Steam pressure of each of the K80 and K90 boilers at the minimum steam output for fuel 1: wood chips- 60% and fuel 2: plant pellets – 40% | MPa(g) | 12 |

  - 4.7 Self-consumption of electricity of K20

This is the self-consumption of the UNIT OB 2 defined part of the K20 boiler part, from the fuel input to the operating silo to the output from the boiler smoke exhaust fan and the ash output on the filter hoppers.

The BIDDER will list the appliances in their offer.

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
| G16 | Self- consumption of electricity at the nominal output of the K20 boiler as an hourly average over 4 hours of operation. | kWh/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

Self- consumption includes all appliances located within the K20 boiler house, including air conditioning, heating, lighting, including the flue gas and air system of the K20 boiler, flue gas cleaning, ash removal, small cooling circuit.

The air compressor station, a supply of belt conveyors within the OB 1 and the fuel management ventilation systems within the OB 1 are excluded from this evaluated group.

  - 4.8 Specific consumption of lime

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G17.1 | Specific consumption of limestone as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G17.2 | Specific consumption of limestone as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G17.3 | Specific consumption of limestone as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.9 Specific consumption of hydrated lime

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G18.1 | Specific consumption of lime hydrate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G18.2 | Specific consumption of hydrated lime as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G18.3 | Specific consumption of hydrated lime as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.10 Specific consumption of sodium bicarbonate

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G19.1 | Specific consumption of sodium bicarbonate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G19.2 | Specific consumption of sodium bicarbonate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G19.3 | Specific consumption of sodium bicarbonate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.11 Specific consumption of sand

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G20.1 | Specific consumption of sand as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G20.2 | Specific consumption of sand as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G20.3 | Specific consumption of sand as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.12 Specific consumption of the aqueous solution of urea

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G21.1 | Specific consumption of the aqueous solution of urea as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G21.2 | Specific consumption of the aqueous solution of urea as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G21.3 | Specific consumption of the aqueous solution of urea as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.13 . Specific consumption of the aqueous solution of ammonium sulphate

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G22.1 | Specific consumption of the aqueous solution of ammonium sulphate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G22.2 | Specific consumption of the aqueous solution of ammonium sulphate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G22.3 | Specific consumption of the aqueous solution of ammonium sulphate as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |

  - 4.14 Specific consumption of the aqueous solution of ammonium

|  | Parameter | Units | The value of the guaranteed parameter | Note |
| --- | --- | --- | --- | --- |
|  | The boiler K20 – fuel 1: wood chips |  |  |  |
| G23.1 | Specific consumption of the aqueous solution of ammonium as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 -Fuel 1: wood chips |  |  |  |
| G23.2 | Specific consumption of the aqueous solution of ammonium as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |
|  | The boilers K80 and K90 for any mixtures of the fuel 1 – 60percent and the fuel 2 – 40percent |  |  |  |
| G23.3 | Specific consumption of the aqueous solution of ammonium as a one hour average over 4 hours at the boiler nominal output | kg/h | TO BE ADDED | according to the value entered in Annex J of the tender documentation |